## LCAX2 Carel
Controller Type | Device Type
LCAX2 Carel | CHILLER
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Flow switch 1 | 01 | 00042 | 01 | 9600 | Digital-Inputs | 1 |  | 2 | 1 | BINARY | Status | Yes
SPPR 1 | 01 | 00043 | 01 | 9600 | Digital-Inputs | 2 |  | 2 | 1 | BINARY | Status | Yes
Oil level switch 1 | 01 | 00044 | 01 | 9600 | Digital-Inputs | 3 |  | 2 | 1 | BINARY | Status | Yes
Comp 1 Switch | 01 | 00045 | 01 | 9600 | Digital-Inputs | 4 |  | 2 | 1 | BINARY | Status | Yes
Flow switch 2 | 01 | 00047 | 01 | 9600 | Digital-Inputs | 5 |  | 2 | 1 | BINARY | Status | Yes
SPPR 2 | 01 | 00048 | 01 | 9600 | Digital-Inputs | 6 |  | 2 | 1 | BINARY | Status | Yes
Oil level switch 2 | 01 | 00049 | 01 | 9600 | Digital-Inputs | 7 |  | 2 | 1 | BINARY | Status | Yes
Comp 2 Switch | 01 | 00050 | 01 | 9600 | Digital-Inputs | 8 |  | 2 | 1 | BINARY | Status | Yes
Unit Switch | 01 | 00052 | 01 | 9600 | Digital-Inputs | 9 |  | 2 | 1 | BINARY | Status | Yes
Compressor 1 On/Off Relay | 01 | 00053 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 1 ULSV 1 Relay | 01 | 00054 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 1 ULSV 2 Relay | 01 | 00055 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 1 ULSV 3 Relay | 01 | 00056 | 01 | 9600 | Relay-Outputs | 4 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Solenoid Valve 1 Relay | 01 | 00057 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 1 system 1 On/Off Relay | 01 | 00058 | 01 | 9600 | Relay-Outputs | 6 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 2 system 1 On/Off Relay | 01 | 00059 | 01 | 9600 | Relay-Outputs | 7 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 1 Oil cooler Relay | 01 | 00060 | 01 | 9600 | Relay-Outputs | 8 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 1 Relay | 01 | 00061 | 01 | 9600 | Relay-Outputs | 9 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 2 On/Off Relay | 01 | 00062 | 01 | 9600 | Relay-Outputs | 10 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 2 ULSV 1 Relay | 01 | 00063 | 01 | 9600 | Relay-Outputs | 11 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 2 ULSV 2 Relay | 01 | 00064 | 01 | 9600 | Relay-Outputs | 12 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 2 ULSV 3 Relay | 01 | 00065 | 01 | 9600 | Relay-Outputs | 13 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Solenoid Valve 2 Relay | 01 | 00066 | 01 | 9600 | Relay-Outputs | 14 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 1 system 2 On/Off Relay | 01 | 00067 | 01 | 9600 | Relay-Outputs | 15 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 2 system 2 On/Off Relay | 01 | 00068 | 01 | 9600 | Relay-Outputs | 16 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Comp 2 Oil cooler Relay | 01 | 00069 | 01 | 9600 | Relay-Outputs | 17 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 2 Relay | 01 | 00070 | 01 | 9600 | Relay-Outputs | 18 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Cooler Water In Temp | 04 | 30002 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Water Out Temp | 04 | 30003 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Suction Pressure 1 | 04 | 30004 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Discharge Pressure 1 | 04 | 30005 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Compressor 1 Current | 04 | 30006 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Discharge Temperature 1 | 04 | 30007 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Water Out Temp 1 | 04 | 30008 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
PT1000 1 | 04 | 30009 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Saturated Suction Temp 1 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Suction Pressure 2 | 04 | 30011 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Discharge Pressure 2 | 04 | 30012 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Compressor 2 Current | 04 | 30013 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Discharge Temperature 2 | 04 | 30014 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Water Out Temp 2 | 04 | 30015 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
PT1000 2 | 04 | 30016 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Saturated Suction Temp 2 | 04 | 30017 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
CW OUT TRGT | 04 | 30036 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No |  |  |  | F
CTRL ZONE+ | 04 | 30037 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No |  |  |  | F
CTRL ZONE- | 04 | 30038 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No |  |  |  | F
FLA COMP#1 | 04 | 30039 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | %
LOampNoSTART | 04 | 30040 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMAL | Periodic | No
HI AMPS | 04 | 30041 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMAL | Periodic | No
FREEZE | 04 | 30044 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
HI DISCH TMP | 04 | 30045 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
DIS TMP UNLD | 04 | 30046 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
DIS TMP RELD | 04 | 30047 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
LOW SUCTION | 04 | 30048 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
LO SUCT UNLD | 04 | 30049 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
LO SUCT RELD | 04 | 30050 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
LOgas LLsFLT | 04 | 30051 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
HI DISC PSI | 04 | 30052 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
HI DISC UNLD | 04 | 30053 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
HI DISC RELD | 04 | 30054 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
Lo DISC PSI | 04 | 30055 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
LOW OIL DIF | 04 | 30056 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
UNSAFE OIL | 04 | 30057 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | PSIG
Liquid Injection On | 04 | 30058 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
ERCON ON | 04 | 30060 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMAL | Periodic | No
CND STG1 ON | 04 | 30062 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
CND STG1 OFF | 04 | 30063 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
CND DIFF ON | 04 | 30064 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
CND DIFF OFF | 04 | 30065 | 01 | 9600 | Setpoints | 26 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
Oil Cooler ON | 04 | 30066 | 01 | 9600 | Setpoints | 27 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
Oil Cooler OFF | 04 | 30067 | 01 | 9600 | Setpoints | 28 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | F
MAX ROC+ | 04 | 30068 | 01 | 9600 | Setpoints | 29 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No
MAX ROC- | 04 | 30069 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No
MAX Demand % | 03 | 40002 | 01 | 9600 | Setpoints | 31 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | %
Step countdown | 03 | 40003 | 01 | 9600 | Setpoints | 32 |  | 4 | 1 | DECIMAL | Periodic | No
Step fall | 03 | 40004 | 01 | 9600 | Setpoints | 33 |  | 4 | 1 | DECIMAL | Periodic | No
Demand loading first | 03 | 40005 | 01 | 9600 | Setpoints | 34 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | Sec
Demand loading second | 03 | 40006 | 01 | 9600 | Setpoints | 35 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | Sec
Actual loading first | 03 | 40007 | 01 | 9600 | Setpoints | 36 |  | 4 | 1 | DECIMAL | Periodic | No
Actual loading second | 03 | 40008 | 01 | 9600 | Setpoints | 37 |  | 4 | 1 | DECIMAL | Periodic | No
Low current initial bypass | 03 | 40016 | 01 | 9600 | Setpoints | 38 |  | 4 | 1 | DECIMAL | Periodic | No
Low suction pressure Initial bypass time | 03 | 40022 | 01 | 9600 | Setpoints | 39 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | Sec
A-CYC ON-ON | 03 | 40035 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No |  |  |  | Sec
Step delay | 03 | 40047 | 01 | 9600 | Setpoints | 41 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | Sec
STEP SENSIT | 03 | 40048 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No
ROC interval | 03 | 40049 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No