## LCAX2-1055D
Controller Type | Device Type
LCAX2-1055D ( Quantam Knits 97422B-B16) | CHILLER
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 1 Relay | 01 | 00002 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Valve 1 Relay | 01 | 00004 | 01 | 9600 | Relay-Outputs | 4 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 1 Relay | 01 | 00005 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan system 1 On/Off Relay | 01 | 00006 | 01 | 9600 | Relay-Outputs | 6 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
ALARM | 01 | 00010 | 01 | 9600 | Relay-Outputs | 7 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 2 On/Off Relay | 01 | 00011 | 01 | 9600 | Relay-Outputs | 8 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 2 Relay | 01 | 00012 | 01 | 9600 | Relay-Outputs | 9 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 2 Relay | 01 | 00013 | 01 | 9600 | Relay-Outputs | 10 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Valve 2 Relay | 01 | 00014 | 01 | 9600 | Relay-Outputs | 11 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 2 Relay | 01 | 00015 | 01 | 9600 | Relay-Outputs | 12 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan system 2 On/Off Relay | 01 | 00016 | 01 | 9600 | Relay-Outputs | 13 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Suction Pressure 1 | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 23 | 70 | PSIG
Discharge Pressure 1 | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 110 | 250 | PSIG
Suction Temperature 1 | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Discharge Temperature 1 | 04 | 30004 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 175 | F
Compressor 1 Current | 04 | 30005 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
SPPR 1 | 04 | 30006 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Cooler Water Out Temp | 04 | 30007 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 39 | 75 | F
Cooler Water In Temp | 04 | 30008 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 44 | 85 | F
Unit Switch | 04 | 30009 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Water Out 1 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Water Out 2 | 04 | 30011 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Liquid Temp 1 | 04 | 30012 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 32 | 65 | F
Flow Switch 1 | 04 | 30013 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | Status | Yes
Oil level switch 1 | 04 | 30014 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 Switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 5 |  | 4 | 1 | DECIMAL | Status | Yes
Flow Switch 2 | 04 | 30016 | 01 | 9600 | Digital-Inputs | 6 |  | 4 | 1 | DECIMAL | Status | Yes
Suction Pressure 2 | 04 | 30017 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 23 | 70 | PSIG
Discharge Pressure 2 | 04 | 30018 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 110 | 250 | PSIG
Suction Temperature 2 | 04 | 30019 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Discharge Temperature 2 | 04 | 30020 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 175 | F
Compressor 2 Current | 04 | 30021 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Oil level switch 2 | 04 | 30022 | 01 | 9600 | Digital-Inputs | 7 |  | 4 | 1 | DECIMAL | Status | Yes
SPPR 2 | 04 | 30023 | 01 | 9600 | Digital-Inputs | 8 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 2 Switch | 04 | 30024 | 01 | 9600 | Digital-Inputs | 9 |  | 4 | 1 | DECIMAL | Status | Yes
Liquid Temp 2 | 04 | 30025 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 32 | 65 | F
BMS RUN | 04 | 30033 | 01 | 9600 | Digital-Inputs | 10 |  | 4 | 1 | DECIMAL | Status | Yes
Suction Superheat 1 | 04 | 30034 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
Suction Superheat 2 | 04 | 30035 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Electronic Expansion Valve 1 | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Electronic Expansion Valve 2 | 04 | 30205 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Chiller State | 04 | 30306 | 01 | 9600 | Control-Information | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 2 State | 04 | 30308 | 01 | 9600 | Control-Information | 3 |  | 4 | 1 | DECIMAL | Status | Yes
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes
Step Delay | 04 | 30317 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec.
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 1 FLA | 04 | 30319 | 01 | 9600 | Control-Information | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 2 FLA | 04 | 30320 | 01 | 9600 | Control-Information | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp 1 | 04 | 30327 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 1 Suction Superheat | 04 | 30328 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
Saturated Discharge Temp 1 | 04 | 30329 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 1 Discharge Superheat | 04 | 30330 | 01 | 9600 | Analog-Inputs | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Saturated Suction Temp 2 | 04 | 30331 | 01 | 9600 | Analog-Inputs | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 2 Suction Superheat | 04 | 30332 | 01 | 9600 | Analog-Inputs | 22 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
Saturated Discharge Temp 2 | 04 | 30333 | 01 | 9600 | Analog-Inputs | 23 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 2 Discharge Superheat | 04 | 30334 | 01 | 9600 | Analog-Inputs | 24 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Oil Pressure Diff 1 | 04 | 30375 | 01 | 9600 | Analog-Inputs | 25 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Oil Pressure Diff 2 | 04 | 30376 | 01 | 9600 | Analog-Inputs | 26 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | Status | Yes
RH Compressor 1 On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Load Solenoid Valve 1 | 04 | 30679 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Unload Solenoid Valve 1 | 04 | 30680 | 01 | 9600 | Runhours | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Liquid Injection Solenoid Valve 1 | 04 | 30681 | 01 | 9600 | Runhours | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Economizer Solenoid Valve 1 | 04 | 30682 | 01 | 9600 | Runhours | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Condenser fan system 1 On/Off | 04 | 30683 | 01 | 9600 | Runhours | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Alarm | 4 | 30687 | 01 | 9600 | Runhours | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Compressor 2 On/Off | 04 | 30688 | 01 | 9600 | Runhours | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Load Solenoid Valve 2 | 04 | 30689 | 01 | 9600 | Runhours | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Unload Solenoid Valve 2 | 04 | 30690 | 01 | 9600 | Runhours | 10 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Liquid Injection Solenoid Valve 2 | 04 | 30691 | 01 | 9600 | Runhours | 11 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Economizer Solenoid Valve 2 | 04 | 30692 | 01 | 9600 | Runhours | 12 |  | 4 | 1 | DECIMAL | Periodic | Yes
RH Condenser fan system 2 On/Off | 04 | 30693 | 01 | 9600 | Runhours | 13 |  | 4 | 1 | DECIMAL | Periodic | Yes
Unit Mode | 4 | 30758 | 1 | 9600 | Control-Information | 10 |  | 4 | 1 | DECIMAL | Periodic | Yes
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
Liq INJECT ON | 03 | 40308 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
SUPERH TARGT | 03 | 40309 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
SUPERH ZONE | 03 | 40310 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV Load DIV | 03 | 40314 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV MAX% | 03 | 40316 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
LO SUPERHEAT | 03 | 40317 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
MAX SLIDE % | 03 | 40330 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MIN SLIDE % | 03 | 40331 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MAX ADJUST % | 03 | 40332 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST % | 03 | 40333 | 01 | 9600 | Setpoints | 26 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
SLIDE SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 27 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
AMP DB HI | 03 | 40335 | 01 | 9600 | Setpoints | 28 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
AMP DB LO | 03 | 40336 | 01 | 9600 | Setpoints | 29 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
LOAD PULSE | 03 | 40337 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
UNLOAD PULSE | 03 | 40338 | 01 | 9600 | Setpoints | 31 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
CND STG1 ON | 03 | 40345 | 01 | 9600 | Setpoints | 32 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND STG1 OFF | 03 | 40346 | 01 | 9600 | Setpoints | 33 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND DIFF ON | 03 | 40347 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND DIFF OFF | 03 | 40348 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CT F MIN RUN | 03 | 40349 | 01 | 9600 | Setpoints | 36 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | PSIG
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC OFF-ON | 03 | 40359 | 01 | 9600 | Setpoints | 38 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
PMP DWN OFF | 03 | 40361 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
PMP DWN DLAY | 03 | 40362 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC ON-ON | 03 | 40363 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | min.
HI AMPS % | 03 | 40375 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas/LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 50 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO DiscSPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 52 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO DISC PSI | 03 | 40385 | 01 | 9600 | Setpoints | 53 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 55 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LOW OIL DIF | 03 | 40391 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
UNSAFE OIL | 03 | 40392 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
SPPR Fault | 03 | 40395 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
ERCON ON% | 03 | 40399 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec.
LEAD COMP | 03 | 40403 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
CMP ROTATION | 03 | 40404 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | D
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LowOil Level | 03 | 40439 | 01 | 9600 | Setpoints | 65 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
LO REF TMP | 03 | 40455 | 01 | 9600 | Setpoints | 66 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO REF UNLD | 03 | 40456 | 01 | 9600 | Setpoints | 67 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 68 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
FLA COMP#2 | 03 | 40472 | 01 | 9600 | Setpoints | 69 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 70 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F

## Status
Register Address | State |  |  | Description
30006 | 0 |  |  | NORMAL
30006 | 1 |  |  | ALARM
30010 | 0 |  |  | ON
30010 | 1 |  |  | OFF
30013 | 0 |  |  | NO FLOW
30013 | 1 |  |  | FLOW
30014 | 0 |  |  | OK
30014 | 1 |  |  | TRIP
30015 | 0 |  |  | ON
30015 | 1 |  |  | OFF
30016 | 0 |  |  | NO FLOW
30016 | 1 |  |  | FLOW
30022 | 0 |  |  | OK
30022 | 1 |  |  | TRIP
30023 | 0 |  |  | NORMAL
30023 | 1 |  |  | ALARM
30024 | 0 |  |  | ON
30024 | 1 |  |  | OFF
30033 | 0 |  |  | STOP
30033 | 1 |  |  | RUN
30306 | 0 |  |  | UNIT IN POWER UP
30306 | 1 |  |  | POWER LOSS DELAY
30306 | 2 |  |  | NO RUN- I/O LOST
30306 | 3 |  |  | UNIT IN LOCKOUT
30306 | 4 |  |  | UNIT IS OFF
30306 | 5 |  |  | UNIT IS HOLDING
30306 | 6 |  |  | UNIT UNLOADING
30306 | 7 |  |  | UNIT IS LOADING
30306 | 8 |  |  | OFF-SMOKE ALARM
30306 | 9 |  |  | RUN/STOP SW OFF
30306 | 10 |  |  | SCHEDULED OFF
30306 | 11 |  |  | OFF-NO FLOW(s)
30306 | 12 |  |  | NOT USED
30306 | 13 |  |  | AMBIENT OFF
30306 | 14 |  |  | PROCESS HEAT OFF
30306 | 15 |  |  | UNIT IS UNLOADED
30306 | 16 |  |  | UNIT IS LOADED
30306 | 17 |  |  | OFF TMP-ICE MADE
30306 | 18 |  |  | ECONOMIZER ONLY
30306 | 19 |  |  | SWITCHING MODES
30306 | 20 |  |  | UNIT SMOKE UNLDG
30306 | 21 |  |  | UNIT OFF UNLDING
30306 | 22 |  |  | UNIT DMD UNLDING
30306 | 23 |  |  | UNIT HEAT UNLDNG
30306 | 24 |  |  | UNLDING RUN CMPS
30306 | 25 |  |  | OPENING BYP VLV
30306 | 26 |  |  | CMP RAMPING UP
30306 | 27 |  |  | CLOSING BYP VLV
30306 | 28 |  |  | FACTORY STARTUP
30306 | 29 |  |  | MAXIMUM RUN TIME
30306 | 30 |  |  | NOT USED
30306 | 31 |  |  | OFF-FIRE ALARM
30306 | 32 |  |  | UNIT HEAT HOLDG
30306 | 33 |  |  | CMP SPD OPTIMIZE
30307 | 0 |  |  | LOST IO LOCKED
30307 | 1 |  |  | CMP LOCKED OUT
30307 | 2 |  |  | SWITCHED OFF
30307 | 3 |  |  | UNLD & PMPDWN
30307 | 4 |  |  | CMP ANTICYCLE
30307 | 5 |  |  | CMP OFF/READY
30307 | 6 |  |  | OIL PMP LUBING
30307 | 7 |  |  | CMP IN STARTUP
30307 | 8 |  |  | CMP UNLOADED
30307 | 9 |  |  | CMP UNLD STEP1
30307 | 10 |  |  | CMP UNLD STEP2
30307 | 11 |  |  | CMP IS HOLDING
30307 | 12 |  |  | CMP IS LOADING
30307 | 13 |  |  | CMP IS UNLDING
30307 | 14 |  |  | CMP IS RUNNING
30307 | 15 |  |  | FAST UNLOADING
30307 | 16 |  |  | LO SUCT UNLOAD
30307 | 17 |  |  | LO SUCT HOLD
30307 | 18 |  |  | HI DISC UNLOAD
30307 | 19 |  |  | HI DISC HOLD
30307 | 20 |  |  | SAFETY TRIPPED
30307 | 21 |  |  | LO TEMP UNLOAD
30307 | 22 |  |  | LO TEMP HOLD
30307 | 23 |  |  | HI AMP HOLD
30307 | 24 |  |  | HI DIS TMP HLD
30307 | 25 |  |  | CMP IS AT 40%
30307 | 26 |  |  | CMP IS AT 70%
30307 | 27 |  |  | HI WATER HOLD
30307 | 28 |  |  | EXTRA 70% STEP
30307 | 29 |  |  | OFF-LO OIL TMP
30307 | 30 |  |  | HI AMP UNLDING
30307 | 31 |  |  | DEF PREPMP OUT
30307 | 32 |  |  | DEFROSTING
30307 | 33 |  |  | DEF PUMP DOWN
30307 | 34 |  |  | HI TEMP UNLOAD
30307 | 35 |  |  | HI TEMP HOLD
30307 | 36 |  |  | SCROLL STEP 1
30307 | 37 |  |  | SCROLL STEP 2
30307 | 38 |  |  | SCROLL STEP 3
30307 | 39 |  |  | SCROLL STEP 4
30307 | 40 |  |  | ON OIL RECOVRY
30307 | 41 |  |  | WAIT P-RATIO
30308 | 0 |  |  | LOST IO LOCKED
30308 | 1 |  |  | CMP LOCKED OUT
30308 | 2 |  |  | SWITCHED OFF
30308 | 3 |  |  | UNLD & PMPDWN
30308 | 4 |  |  | CMP ANTICYCLE
30308 | 5 |  |  | CMP OFF/READY
30308 | 6 |  |  | OIL PMP LUBING
30308 | 7 |  |  | CMP IN STARTUP
30308 | 8 |  |  | CMP UNLOADED
30308 | 9 |  |  | CMP UNLD STEP1
30308 | 10 |  |  | CMP UNLD STEP2
30308 | 11 |  |  | CMP IS HOLDING
30308 | 12 |  |  | CMP IS LOADING
30308 | 13 |  |  | CMP IS UNLDING
30308 | 14 |  |  | CMP IS RUNNING
30308 | 15 |  |  | FAST UNLOADING
30308 | 16 |  |  | LO SUCT UNLOAD
30308 | 17 |  |  | LO SUCT HOLD
30308 | 18 |  |  | HI DISC UNLOAD
30308 | 19 |  |  | HI DISC HOLD
30308 | 20 |  |  | SAFETY TRIPPED
30308 | 21 |  |  | LO TEMP UNLOAD
30308 | 22 |  |  | LO TEMP HOLD
30308 | 23 |  |  | HI AMP HOLD
30308 | 24 |  |  | HI DIS TMP HLD
30308 | 25 |  |  | CMP IS AT 40%
30308 | 26 |  |  | CMP IS AT 70%
30308 | 27 |  |  | HI WATER HOLD
30308 | 28 |  |  | EXTRA 70% STEP
30308 | 29 |  |  | OFF-LO OIL TMP
30308 | 30 |  |  | HI AMP UNLDING
30308 | 31 |  |  | DEF PREPMP OUT
30308 | 32 |  |  | DEFROSTING
30308 | 33 |  |  | DEF PUMP DOWN
30308 | 34 |  |  | HI TEMP UNLOAD
30308 | 35 |  |  | HI TEMP HOLD
30308 | 36 |  |  | SCROLL STEP 1
30308 | 37 |  |  | SCROLL STEP 2
30308 | 38 |  |  | SCROLL STEP 3
30308 | 39 |  |  | SCROLL STEP 4
30308 | 40 |  |  | ON OIL RECOVRY
30308 | 41 |  |  | WAIT P-RATIO
Register Address Type | Alarm Type | Register Address Point | Alarm Point | Description
30668 | 0 | 30673 | Not Used (255) | POWER FAILED
30668 | 1 | 30673 | Not Used (255) | COMPUTER RESET
30668 | 2 | 30673 | Not Used (255) | BATTERY FAILED
30668 | 3 | 30673 | Not Used (255) | INVERTER TEMP
30668 | 4 | 30673 | Not Used (255) | DISCHARGE TEMP
30668 | 5 | 30673 | Not Used (255) | SUCTION PSI
30668 | 6 | 30673 | Not Used (255) | DISCHARGE PSI
30668 | 7 | 30673 | Not Used (255) | 3PHASE OVER AMPS
30668 | 8 | 30673 | Not Used (255) | ALARMS CLEARED
30668 | 9 | 30673 | Not Used (255) | POWER RETURNED
30668 | 10 | 30673 | Not Used (255) | CAVITY TEMP
30668 | 11 | 30673 | Not Used (255) | STPT CHANGED
30668 | 12 | 30673 | Not Used (255) | RO TO MANON
30668 | 13 | 30673 | Not Used (255) | AO TO MANUAL
30668 | 14 | 30673 | Not Used (255) | SI TO MANUAL
30668 | 15 | 30673 | Not Used (255) | POINT INFO CLEAR
30668 | 16 | 30673 | Not Used (255) | CLOCK SET
30668 | 17 | 30673 | Not Used (255) | CFG DOWNLOADED
30668 | 18 | 30673 | Not Used (255) | ROTATED LEAD\0
30668 | 19 | 30673 | Not Used (255) | SI OFFSET
30668 | 20 | 30673 | Not Used (255) | SI TYPE
30668 | 21 | 30673 | Not Used (255) | LEAV FLUID TEMP
30668 | 22 | 30673 | Not Used (255) | PRESSURE RATIO
30668 | 23 | 30673 | Not Used (255) | BEAR MOTOR CMP
30668 | 24 | 30673 | Not Used (255) | CMP SENSOR FLT
30668 | 25 | 30673 | Not Used (255) | DAYLIGHT SAVINGS
30668 | 26 | 30673 | Not Used (255) | LOCKOUT RESET
30668 | 27 | 30673 | Not Used (255) | FIRMWARE LOADED
30668 | 28 | 30673 | Not Used (255) | BOOTLOADER ERROR
30668 | 29 | 30673 | Not Used (255) | RS485 CHANGED
30668 | 30 | 30673 | Not Used (255) | ETHERNET CHANGED
30668 | 31 | 30673 | Not Used (255) | INVALID CFG CSUM
30668 | 32 | 30673 | Not Used (255) | INVALID CFG VER
30668 | 33 | 30673 | Not Used (255) | LOST RO COMM
30668 | 34 | 30673 | Not Used (255) | LOST SI COMM
30668 | 35 | 30673 | Not Used (255) | UNUSED
30668 | 36 | 30673 | Not Used (255) | WATCHDOG RESET
30668 | 37 | 30673 | Not Used (255) | SRC TEMP FAULT
30668 | 38 | 30673 | Not Used (255) | EMERGENCY STOP
30668 | 39 | 30673 | Not Used (255) | OFF-SMOKE ALARM
30668 | 40 | 30673 | Not Used (255) | RO TO AUTO
30668 | 41 | 30673 | Not Used (255) | AO TO AUTO
30668 | 42 | 30673 | Not Used (255) | SI TO AUTO
30668 | 43 | 30673 | Not Used (255) | PHASE LOSS
30668 | 44 | 30673 | Not Used (255) | RO TO MANOFF
30668 | 45 | 30673 | Not Used (255) | Spare
30668 | 46 | 30673 | Not Used (255) | Spare
30668 | 47 | 30673 | Not Used (255) | Spare
30668 | 48 | 30673 | Not Used (255) | Spare
30668 | 49 | 30673 | Not Used (255) | Spare
30668 | 50 | 30673 | Not Used (255) | LOST IO SHUTDOWN
30668 | 51 | 30673 | Not Used (255) | SMOKE PURGE
30668 | 52 | 30673 | Not Used (255) | INVALID CFG TYPE
30668 | 53 | 30673 | Not Used (255) | HEAT WHEEL ALARM
30668 | 54 | 30673 | Not Used (255) | LOST I/O RESTART
30668 | 55 | 30673 | Not Used (255) | OFF-FIRE ALARM
30668 | 56 | 30673 | Not Used (255) | UNUSED ALARM #56
30668 | 57 | 30673 | Not Used (255) | PURGE RESTART
30668 | 58 | 30673 | Not Used (255) | TMP OFF-ICE MADE
30668 | 59 | 30673 | Not Used (255) | LVL OFF-ICE MADE
30668 | 60 | 30673 | Not Used (255) | START MAKING ICE
30668 | 61 | 30673 | Not Used (255) | INTERNAL RAM
30668 | 62 | 30673 | Not Used (255) | EXTERNAL RAM 0
30668 | 63 | 30673 | Not Used (255) | EXTERNAL RAM 1
30668 | 64 | 30673 | Not Used (255) | LOST A/D CONVTR
30668 | 65 | 30673 | Not Used (255) | LOST DISPLAY
30668 | 66 | 30673 | Not Used (255) | LOST IO COMP
30668 | 67 | 30673 | Not Used (255) | LOST KEYPAD
30668 | 68 | 30673 | Not Used (255) | CFG FLASH PTR
30668 | 69 | 30673 | Not Used (255) | NETWORK ADDR CHG
30668 | 70 | 30673 | Not Used (255) | UPDATE FLASHCFG
30668 | 71 | 30673 | Not Used (255) | LOST A/D SHUTDWN
30668 | 72 | 30673 | Not Used (255) | CF CARD REMOVED
30668 | 73 | 30673 | Not Used (255) | CF CARD INSERTED
30668 | 74 | 30673 | Not Used (255) | CF INIT ERROR
30668 | 75 | 30673 | Not Used (255) | MCS-STAT OFFLINE
30668 | 76 | 30673 | Not Used (255) | BACnet DEVICE ID
30668 | 77 | 30673 | Not Used (255) | FORCE MCS PRTCOL
30668 | 78 | 30673 | Not Used (255) | UNUSED ALARM #78
30668 | 79 | 30673 | Not Used (255) | UNUSED ALARM #79
30668 | 80 | 30673 | 1 or 2 | CW OUT TRGT
30668 | 81 | 30673 | 1 or 2 | CTRL ZONE+
30668 | 82 | 30673 | 1 or 2 | CTRL ZONE-
30668 | 87 | 30673 | 1 or 2 | L.INJECT ON
30668 | 88 | 30673 | 1 or 2 | SUPER HEAT TARG
30668 | 89 | 30673 | 1 or 2 | SUPER HEAT ZONE
30668 | 90 | 30673 | 1 or 2 | EXV LOAD ADJ
30668 | 91 | 30673 | 1 or 2 | EXV FINE ADJ
30668 | 92 | 30673 | 1 or 2 | EXV COURSE
30668 | 93 | 30673 | 1 or 2 | EXV Load DIV
30668 | 94 | 30673 | 1 or 2 | EXV MIN%
30668 | 95 | 30673 | 1 or 2 | EXV MAX%
30668 | 96 | 30673 | 1 or 2 | LO SUPERHEAT
30668 | 97 | 30673 | 1 or 2 | LOSUCTPSIDLY
30668 | 98 | 30673 | 1 or 2 | EXV DELAY
30668 | 99 | 30673 | 1 or 2 | EXV STRT TME
30668 | 102 | 30673 | 1 or 2 | POWERUP DLAY
30668 | 104 | 30673 | 1 or 2 | STEP SENSIT
30668 | 105 | 30673 | 1 or 2 | STEP DELAY
30668 | 106 | 30673 | 1 or 2 | MAX ROC-
30668 | 107 | 30673 | 1 or 2 | MAX ROC+
30668 | 108 | 30673 | 1 or 2 | ROC INTERVAL
30668 | 109 | 30673 | 1 or 2 | MAX SLIDE %
30668 | 110 | 30673 | 1 or 2 | MIN SLIDE %
30668 | 111 | 30673 | 1 or 2 | MAX ADJUST %
30668 | 112 | 30673 | 1 or 2 | MIN ADJUST %
30668 | 113 | 30673 | 1 or 2 | SLIDE SENSIT
30668 | 114 | 30673 | 1 or 2 | AMP DB HI
30668 | 115 | 30673 | 1 or 2 | AMP DB LO
30668 | 116 | 30673 | 1 or 2 | LOAD PULSE
30668 | 117 | 30673 | 1 or 2 | UNLOAD PULSE
30668 | 124 | 30673 | 1 or 2 | CND STG1 ON
30668 | 125 | 30673 | 1 or 2 | CND STG1 OFF
30668 | 126 | 30673 | 1 or 2 | CND DIFF ON
30668 | 127 | 30673 | 1 or 2 | CND DIFF OFF
30668 | 128 | 30673 | 1 or 2 | CND MIN RUN
30668 | 135 | 30673 | 1 or 2 | PULSE DELAY
30668 | 138 | 30673 | 1 or 2 | A-CYC OFF-ON
30668 | 140 | 30673 | 1 or 2 | PMP DWN OFF
30668 | 141 | 30673 | 1 or 2 | PMP DWN DLAY
30668 | 142 | 30673 | 1 or 2 | A-CYC ON-ON
30668 | 143 | 30673 | 1 or 2 | COMP MIN RUN
30668 | 152 | 30673 | 1 or 2 | PartWindDely
30668 | 154 | 30673 | 1 or 2 | HI AMPS %
30668 | 155 | 30673 | 1 or 2 | LOampNoSTART
30668 | 156 | 30673 | 1 or 2 | LOW SUCTION
30668 | 157 | 30673 | 1 or 2 | LO SUCT UNLD
30668 | 158 | 30673 | 1 or 2 | LO SUCT RELD
30668 | 159 | 30673 | 1 or 2 | LOgas/LLsFLT
30668 | 160 | 30673 | 1 or 2 | HI DISC PSI
30668 | 161 | 30673 | 1 or 2 | HI DISC UNLD
30668 | 162 | 30673 | 1 or 2 | HI DISC RELD
30668 | 163 | 30673 | 1 or 2 | LO DiscSPRHT
30668 | 164 | 30673 | 1 or 2 | LO DISC PSI
30668 | 166 | 30673 | 1 or 2 | HI DISCH TMP
30668 | 167 | 30673 | 1 or 2 | DIS TMP UNLD
30668 | 168 | 30673 | 1 or 2 | DIS TMP RELD
30668 | 170 | 30673 | 1 or 2 | LOW OIL DIF
30668 | 171 | 30673 | 1 or 2 | UNSAFE OIL
30668 | 174 | 30673 | 1 or 2 | SPPR Fault
30668 | 178 | 30673 | 1 or 2 | ERCON ON%
30668 | 180 | 30673 | 1 or 2 | SafetyHold
30668 | 182 | 30673 | 1 or 2 | LEAD COMP
30668 | 183 | 30673 | 1 or 2 | CMP ROTATION
30668 | 190 | 30673 | 1 or 2 | FREEZE
30668 | 218 | 30673 | 1 or 2 | LowOil Level
30668 | 234 | 30673 | 1 or 2 | lo liq temp
30668 | 235 | 30673 | 1 or 2 | lo liq unld
30668 | 250 | 30673 | 1 or 2 | FLA COMP#1
30668 | 251 | 30673 | 1 or 2 | FLA COMP#2
30668 | 281 | 30673 | 1 or 2 | HI EVP DEL T
30668 | 310 | 30673 | 0 | Alarm SI SP1
30668 | 310 | 30673 | 1 | Alarm SI DP1
30668 | 310 | 30673 | 2 | Alarm SI ST1
30668 | 310 | 30673 | 3 | Alarm SI DT1
30668 | 310 | 30673 | 4 | Alarm SI AMPS1
30668 | 310 | 30673 | 5 | Alarm SI SPPR1
30668 | 310 | 30673 | 6 | Alarm SI WAT OUT
30668 | 310 | 30673 | 7 | Alarm SI WATER IN
30668 | 310 | 30673 | 8 | Alarm SI RUN/STOP
30668 | 310 | 30673 | 9 | ALARM Leaving 1
30668 | 310 | 30673 | 10 | ALARM Leaving 2
30668 | 310 | 30673 | 11 | ALARM Liq temp 1
30668 | 310 | 30673 | 12 | Alarm SI FLOW SW 1
30668 | 310 | 30673 | 13 | Alarm SI OIL LEVEL1
30668 | 310 | 30673 | 14 | ALARM SYS1OFF
30668 | 310 | 30673 | 15 | Alarm SI FLOW SW 2
30668 | 310 | 30673 | 16 | Alarm SI SP2
30668 | 310 | 30673 | 17 | Alarm SI DP2
30668 | 310 | 30673 | 18 | Alarm SI ST2
30668 | 310 | 30673 | 19 | Alarm SI DT2
30668 | 310 | 30673 | 20 | Alarm SI AMPS2
30668 | 310 | 30673 | 21 | Alarm SI OIL LEVEL2
30668 | 310 | 30673 | 22 | Alarm SI SPPR2
30668 | 310 | 30673 | 23 | ALARM SYS2OFF
30668 | 310 | 30673 | 24 | ALARM Liq temp 1