## LCAX2-180 DEF
Controller Type | Device Type | Chiller Code
LCAX2-180DEF (SRL 1733C08) | CHILLER | 1
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 M On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 1 P On/Off Relay | 01 | 00002 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 1 Relay | 01 | 00004 | 01 | 9600 | Relay-Outputs | 4 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Valve 1 Relay | 01 | 00005 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 1 Relay | 01 | 00006 | 01 | 9600 | Relay-Outputs | 6 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
HGBP Solenoid Valve 1 Relay | 01 | 00007 | 01 | 9600 | Relay-Outputs | 7 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 1 system 1 On/Off Relay | 01 | 00009 | 01 | 9600 | Relay-Outputs | 8 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 2 system 1 On/Off Relay | 01 | 00010 | 01 | 9600 | Relay-Outputs | 9 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 2 M On/Off Relay | 01 | 00011 | 01 | 9600 | Relay-Outputs | 10 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 2 P On/Off Relay | 01 | 00012 | 01 | 9600 | Relay-Outputs | 11 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 2 Relay | 01 | 00013 | 01 | 9600 | Relay-Outputs | 12 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 2 Relay | 01 | 00014 | 01 | 9600 | Relay-Outputs | 13 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 2 Relay | 01 | 00015 | 01 | 9600 | Relay-Outputs | 14 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 1 system 2 On/Off Relay | 01 | 00016 | 01 | 9600 | Relay-Outputs | 15 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Condenser fan 2 system 2 On/Off Relay | 01 | 00017 | 01 | 9600 | Relay-Outputs | 16 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
HGBP Solenoid Valve 2 Relay | 01 | 00018 | 01 | 9600 | Relay-Outputs | 17 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Suction Pressure 1 | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 23 | 70 | PSIG
Discharge Pressure 1 | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 110 | 250 | PSIG
Suction Temperature 1 | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Compressor 1 Current | 04 | 30005 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
SPPR 1 | 04 | 30006 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Cooler Water Out Temp | 04 | 30007 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 39 | 75 | F
Cooler Water In Temp | 04 | 30008 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 44 | 85 | F
Unit Switch | 04 | 30009 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Discharge Temperature 1 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 175 | F
Flow Switch | 04 | 30013 | 01 | 9600 | Digital-Inputs | 5 |  | 4 | 1 | DECIMAL | Status | Yes
Oil level switch 1 | 04 | 30014 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 Switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | Status | Yes
Suction Pressure 2 | 04 | 30017 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 23 | 70 | PSIG
Discharge Pressure 2 | 04 | 30018 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 110 | 250 | PSIG
Suction Temperature 2 | 04 | 30019 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Discharge Temperature 2 | 04 | 30020 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 175 | F
Compressor 2 Current | 04 | 30021 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Oil level switch 2 | 04 | 30022 | 01 | 9600 | Digital-Inputs | 6 |  | 4 | 1 | DECIMAL | Status | Yes
SPPR 2 | 04 | 30023 | 01 | 9600 | Digital-Inputs | 7 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 2 Switch | 04 | 30024 | 01 | 9600 | Digital-Inputs | 8 |  | 4 | 1 | DECIMAL | Status | Yes
BMS RUN | 04 | 30033 | 01 | 9600 | Digital-Inputs | 9 |  | 4 | 1 | DECIMAL | Status | Yes
SSH 1 | 04 | 30034 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
SSH 2 | 04 | 30035 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Electronic Expansion Valve 1 | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Electronic Expansion Valve 2 | 04 | 30205 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Chiller State | 04 | 30306 | 01 | 9600 | Control-Information | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 2 State | 04 | 30308 | 01 | 9600 | Control-Information | 3 |  | 4 | 1 | DECIMAL | Status | Yes
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes
Step Delay | 04 | 30317 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec.
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 1 FLA | 04 | 30319 | 01 | 9600 | Control-Information | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 2 FLA | 04 | 30320 | 01 | 9600 | Control-Information | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp 1 | 04 | 30327 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 1 Suction Superheat | 04 | 30328 | 01 | 9600 | Analog-Inputs | 116 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
Saturated Discharge Temp 1 | 04 | 30329 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 1 Discharge Superheat | 04 | 30330 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Saturated Suction Temp 2 | 04 | 30331 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 2 Suction Superheat | 04 | 30332 | 01 | 9600 | Analog-Inputs | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | -5 | 25 | F
Saturated Discharge Temp 2 | 04 | 30333 | 01 | 9600 | Analog-Inputs | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Comp 2 Discharge Superheat | 04 | 30334 | 01 | 9600 | Analog-Inputs | 22 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 60 | F
Oil Pressure Diff 1 | 04 | 30375 | 01 | 9600 | Analog-Inputs | 23 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Oil Pressure Diff 2 | 04 | 30376 | 01 | 9600 | Analog-Inputs | 24 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | Status | Yes
RH Compressor 1 M On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Compressor 1 P On/Off | 04 | 30679 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Load Solenoid Valve 1 | 04 | 30680 | 01 | 9600 | Runhours | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Unload Solenoid Valve 1 | 04 | 30681 | 01 | 9600 | Runhours | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Liquid Injection Solenoid Valve 1 | 04 | 30682 | 01 | 9600 | Runhours | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Economizer Solenoid Valve 1 | 04 | 30683 | 01 | 9600 | Runhours | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH HGBP Solenoid Valve 1 | 04 | 30684 | 01 | 9600 | Runhours | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Condenser fan 1 system 1 On/Off | 04 | 30686 | 01 | 9600 | Runhours | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Condenser fan 2 system 1 On/Off | 04 | 30687 | 01 | 9600 | Runhours | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Compressor 2 M On/Off | 04 | 30688 | 01 | 9600 | Runhours | 10 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Compressor 2 P On/Off | 04 | 30689 | 01 | 9600 | Runhours | 11 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Load Solenoid Valve 2 | 04 | 30690 | 01 | 9600 | Runhours | 12 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Unload Solenoid Valve 2 | 04 | 30691 | 01 | 9600 | Runhours | 13 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Economizer Solenoid Valve 2 | 04 | 30692 | 01 | 9600 | Runhours | 14 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Condenser fan 1 system 2 On/Off | 04 | 30693 | 01 | 9600 | Runhours | 15 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH Condenser fan 2 system 2 On/Off | 04 | 30694 | 01 | 9600 | Runhours | 16 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
RH HGBP Solenoid Valve 2 | 04 | 30695 | 01 | 9600 | Runhours | 17 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs
Unit Mode | 04 | 30758 | 01 | 9600 | Control-Information | 10 |  | 4 | 1 | DECIMAL | Status | Yes
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
Liq INJECT ON | 03 | 40308 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
SUPERH TARGT | 03 | 40309 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
ZONE+ /- | 03 | 40310 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV Load DIV | 03 | 40314 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV MAX% | 03 | 40316 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
LO SUPERHEAT | 03 | 40317 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
MAX SLIDE % | 03 | 40330 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MIN SLIDE % | 03 | 40331 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MAX ADJUST % | 03 | 40332 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST % | 03 | 40333 | 01 | 9600 | Setpoints | 26 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
SLIDE SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 27 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
AMP DB HI | 03 | 40335 | 01 | 9600 | Setpoints | 28 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
AMP DB LO | 03 | 40336 | 01 | 9600 | Setpoints | 29 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
LOAD PULSE | 03 | 40337 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
UNLOAD PULSE | 03 | 40338 | 01 | 9600 | Setpoints | 31 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
CND STG1 ON | 03 | 40345 | 01 | 9600 | Setpoints | 32 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND STG1 OFF | 03 | 40346 | 01 | 9600 | Setpoints | 33 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND DIFF ON | 03 | 40347 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND DIFF OFF | 03 | 40348 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
CND MIN RUN | 03 | 40349 | 01 | 9600 | Setpoints | 36 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | min.
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC OFF-ON | 03 | 40359 | 01 | 9600 | Setpoints | 38 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
PMP DWN OFF | 03 | 40361 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
PMP DWN DLAY | 03 | 40362 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC ON-ON | 03 | 40363 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | min.
PartWindDely | 03 | 40373 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
HI AMPS % | 03 | 40375 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas/LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 50 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 52 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO DiscSPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 53 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO DISC PSI | 03 | 40385 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 55 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LOW OIL DIF | 03 | 40391 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
UNSAFE OIL | 03 | 40392 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
SPPR Fault | 03 | 40395 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
ERCON ON% | 03 | 40399 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec.
LEAD COMP | 03 | 40403 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
CMP ROTATION | 03 | 40404 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | D
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 65 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LowOil Level | 03 | 40439 | 01 | 9600 | Setpoints | 66 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 67 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
FLA COMP#2 | 03 | 40472 | 01 | 9600 | Setpoints | 68 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 69 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F

## Status
Register Address | State |  |  | Description
30006 | 0 |  |  | NORMAL
30006 | 1 |  |  | ALARM
30009 | 0 |  |  | ON
30009 | 1 |  |  | OFF
30013 | 0 |  |  | NO FLOW
30013 | 1 |  |  | FLOW
30014 | 0 |  |  | OK
30014 | 1 |  |  | TRIP
30015 | 0 |  |  | ON
30015 | 1 |  |  | OFF
30022 | 0 |  |  | OK
30022 | 1 |  |  | TRIP
30023 | 0 |  |  | NORMAL
30023 | 1 |  |  | ALARM
30024 | 0 |  |  | ON
30024 | 1 |  |  | OFF
30033 | 0 |  |  | STOP
30033 | 1 |  |  | RUN
30306 | 0 |  |  | UNIT IN POWER UP
30306 | 1 |  |  | POWER LOSS DELAY
30306 | 2 |  |  | NO RUN- I/O LOST
30306 | 3 |  |  | UNIT IN LOCKOUT
30306 | 4 |  |  | UNIT IS OFF
30306 | 5 |  |  | UNIT IS HOLDING
30306 | 6 |  |  | UNIT UNLOADING
30306 | 7 |  |  | UNIT IS LOADING
30306 | 8 |  |  | OFF-SMOKE ALARM
30306 | 9 |  |  | RUN/STOP SW OFF
30306 | 10 |  |  | SCHEDULED OFF
30306 | 11 |  |  | OFF-NO FLOW(s)
30306 | 12 |  |  | NOT USED
30306 | 13 |  |  | AMBIENT OFF
30306 | 14 |  |  | PROCESS HEAT OFF
30306 | 15 |  |  | UNIT IS UNLOADED
30306 | 16 |  |  | UNIT IS LOADED
30306 | 17 |  |  | OFF TMP-ICE MADE
30306 | 18 |  |  | ECONOMIZER ONLY
30306 | 19 |  |  | SWITCHING MODES
30306 | 20 |  |  | UNIT SMOKE UNLDG
30306 | 21 |  |  | UNIT OFF UNLDING
30306 | 22 |  |  | UNIT DMD UNLDING
30306 | 23 |  |  | UNIT HEAT UNLDNG
30306 | 24 |  |  | UNLDING RUN CMPS
30306 | 25 |  |  | OPENING BYP VLV
30306 | 26 |  |  | CMP RAMPING UP
30306 | 27 |  |  | CLOSING BYP VLV
30306 | 28 |  |  | FACTORY STARTUP
30306 | 29 |  |  | MAXIMUM RUN TIME
30306 | 30 |  |  | NOT USED
30306 | 31 |  |  | OFF-FIRE ALARM
30306 | 32 |  |  | UNIT HEAT HOLDG
30306 | 33 |  |  | CMP SPD OPTIMIZE
30307 | 0 |  |  | LOST IO LOCKED
30307 | 1 |  |  | CMP LOCKED OUT
30307 | 2 |  |  | SWITCHED OFF
30307 | 3 |  |  | UNLD & PMPDWN
30307 | 4 |  |  | CMP ANTICYCLE
30307 | 5 |  |  | CMP OFF/READY
30307 | 6 |  |  | OIL PMP LUBING
30307 | 7 |  |  | CMP IN STARTUP
30307 | 8 |  |  | CMP UNLOADED
30307 | 9 |  |  | CMP UNLD STEP1
30307 | 10 |  |  | CMP UNLD STEP2
30307 | 11 |  |  | CMP IS HOLDING
30307 | 12 |  |  | CMP IS LOADING
30307 | 13 |  |  | CMP IS UNLDING
30307 | 14 |  |  | CMP IS RUNNING
30307 | 15 |  |  | FAST UNLOADING
30307 | 16 |  |  | LO SUCT UNLOAD
30307 | 17 |  |  | LO SUCT HOLD
30307 | 18 |  |  | HI DISC UNLOAD
30307 | 19 |  |  | HI DISC HOLD
30307 | 20 |  |  | SAFETY TRIPPED
30307 | 21 |  |  | LO TEMP UNLOAD
30307 | 22 |  |  | LO TEMP HOLD
30307 | 23 |  |  | HI AMP HOLD
30307 | 24 |  |  | HI DIS TMP HLD
30307 | 25 |  |  | CMP IS AT 40%
30307 | 26 |  |  | CMP IS AT 70%
30307 | 27 |  |  | HI WATER HOLD
30307 | 28 |  |  | EXTRA 70% STEP
30307 | 29 |  |  | OFF-LO OIL TMP
30307 | 30 |  |  | HI AMP UNLDING
30307 | 31 |  |  | DEF PREPMP OUT
30307 | 32 |  |  | DEFROSTING
30307 | 33 |  |  | DEF PUMP DOWN
30307 | 34 |  |  | HI TEMP UNLOAD
30307 | 35 |  |  | HI TEMP HOLD
30307 | 36 |  |  | SCROLL STEP 1
30307 | 37 |  |  | SCROLL STEP 2
30307 | 38 |  |  | SCROLL STEP 3
30307 | 39 |  |  | SCROLL STEP 4
30307 | 40 |  |  | ON OIL RECOVRY
30307 | 41 |  |  | WAIT P-RATIO
30307 | 42 |  |  | CMP GROUP OFF
30308 | 0 |  |  | LOST IO LOCKED
30308 | 1 |  |  | CMP LOCKED OUT
30308 | 2 |  |  | SWITCHED OFF
30308 | 3 |  |  | UNLD & PMPDWN
30308 | 4 |  |  | CMP ANTICYCLE
30308 | 5 |  |  | CMP OFF/READY
30308 | 6 |  |  | OIL PMP LUBING
30308 | 7 |  |  | CMP IN STARTUP
30308 | 8 |  |  | CMP UNLOADED
30308 | 9 |  |  | CMP UNLD STEP1
30308 | 10 |  |  | CMP UNLD STEP2
30308 | 11 |  |  | CMP IS HOLDING
30308 | 12 |  |  | CMP IS LOADING
30308 | 13 |  |  | CMP IS UNLDING
30308 | 14 |  |  | CMP IS RUNNING
30308 | 15 |  |  | FAST UNLOADING
30308 | 16 |  |  | LO SUCT UNLOAD
30308 | 17 |  |  | LO SUCT HOLD
30308 | 18 |  |  | HI DISC UNLOAD
30308 | 19 |  |  | HI DISC HOLD
30308 | 20 |  |  | SAFETY TRIPPED
30308 | 21 |  |  | LO TEMP UNLOAD
30308 | 22 |  |  | LO TEMP HOLD
30308 | 23 |  |  | HI AMP HOLD
30308 | 24 |  |  | HI DIS TMP HLD
30308 | 25 |  |  | CMP IS AT 40%
30308 | 26 |  |  | CMP IS AT 70%
30308 | 27 |  |  | HI WATER HOLD
30308 | 28 |  |  | EXTRA 70% STEP
30308 | 29 |  |  | OFF-LO OIL TMP
30308 | 30 |  |  | HI AMP UNLDING
30308 | 31 |  |  | DEF PREPMP OUT
30308 | 32 |  |  | DEFROSTING
30308 | 33 |  |  | DEF PUMP DOWN
30308 | 34 |  |  | HI TEMP UNLOAD
30308 | 35 |  |  | HI TEMP HOLD
30308 | 36 |  |  | SCROLL STEP 1
30308 | 37 |  |  | SCROLL STEP 2
30308 | 38 |  |  | SCROLL STEP 3
30308 | 39 |  |  | SCROLL STEP 4
30308 | 40 |  |  | ON OIL RECOVRY
30308 | 41 |  |  | WAIT P-RATIO
30307 | 42 |  |  | CMP GROUP OFF
Register Address Type | Status/ Alarm Type | Register Address Point | Alarm Point | Description
30668 | 0 | 30673 | 1 | POWER FAILED
30668 | 1 | 30673 | 2 | COMPUTER RESET
30668 | 2 | 30673 | 3 | BATTERY FAILED
30668 | 3 | 30673 | 4 | INVERTER TEMP
30668 | 4 | 30673 | 5 | DISCHARGE TEMP
30668 | 5 | 30673 | 6 | SUCTION PSI
30668 | 6 | 30673 | 7 | DISCHARGE PSI
30668 | 7 | 30673 | 8 | 3PHASE OVER AMPS
30668 | 8 | 30673 | 9 | ALARMS CLEARED
30668 | 9 | 30673 | 10 | POWER RETURNED
30668 | 10 | 30673 | 11 | CAVITY TEMP
30668 | 11 | 30673 | 12 | STPT CHANGED
30668 | 12 | 30673 | 13 | RO TO MANON
30668 | 13 | 30673 | 14 | AO TO MANUAL
30668 | 14 | 30673 | 15 | SI TO MANUAL
30668 | 15 | 30673 | 16 | POINT INFO CLEAR
30668 | 16 | 30673 | 17 | CLOCK SET
30668 | 17 | 30673 | 18 | CFG DOWNLOADED
30668 | 18 | 30673 | 19 | ROTATED LEAD\0
30668 | 19 | 30673 | 20 | SI OFFSET
30668 | 20 | 30673 | 21 | SI TYPE
30668 | 21 | 30673 | 22 | LEAV FLUID TEMP
30668 | 22 | 30673 | 23 | PRESSURE RATIO
30668 | 23 | 30673 | 24 | BEAR MOTOR CMP
30668 | 24 | 30673 | 25 | CMP SENSOR FLT
30668 | 25 | 30673 | 26 | DAYLIGHT SAVINGS
30668 | 26 | 30673 | 27 | LOCKOUT RESET
30668 | 27 | 30673 | 28 | FIRMWARE LOADED
30668 | 28 | 30673 | 29 | BOOTLOADER ERROR
30668 | 29 | 30673 | 30 | RS485 CHANGED
30668 | 30 | 30673 | 31 | ETHERNET CHANGED
30668 | 31 | 30673 | 32 | INVALID CFG CSUM
30668 | 32 | 30673 | 33 | INVALID CFG VER
30668 | 33 | 30673 | 34 | LOST RO COMM
30668 | 34 | 30673 | 35 | LOST SI COMM
30668 | 35 | 30673 | 36 | BACnet Port Chg
30668 | 36 | 30673 | 37 | WATCHDOG RESET
30668 | 37 | 30673 | 38 | SRC TEMP FAULT
30668 | 38 | 30673 | 39 | EMERGENCY STOP
30668 | 39 | 30673 | 40 | OFF-SMOKE ALARM
30668 | 40 | 30673 | 41 | RO TO AUTO
30668 | 41 | 30673 | 42 | AO TO AUTO
30668 | 42 | 30673 | 43 | SI TO AUTO
30668 | 43 | 30673 | 44 | PHASE LOSS
30668 | 44 | 30673 | 45 | RO TO MANOFF
30668 | 45 | 30673 | 46 | TURBO LOCK OUT
30668 | 46 | 30673 | 47 | TURBO WIND TMP
30668 | 47 | 30673 | 48 | TURBOCOR SSH FLT
30668 | 48 | 30673 | 49 | TURB RESERVED
30668 | 49 | 30673 | 50 | CND/CTG FAULT
30668 | 50 | 30673 | 51 | LOST IO SHUTDOWN
30668 | 51 | 30673 | 52 | SMOKE PURGE
30668 | 52 | 30673 | 53 | INVALID CFG TYPE
30668 | 53 | 30673 | 54 | ENGY WHEEL ALARM
30668 | 54 | 30673 | 55 | LOST I/O RESTART
30668 | 55 | 30673 | 56 | OFF-FIRE ALARM
30668 | 56 | 30673 | 57 | NO IGNITION
30668 | 57 | 30673 | 58 | PURGE RESTART
30668 | 58 | 30673 | 59 | TMP OFF-ICE MADE
30668 | 59 | 30673 | 60 | LVL OFF-ICE MADE
30668 | 60 | 30673 | 61 | START MAKING ICE
30668 | 61 | 30673 | 62 | INTERNAL RAM
30668 | 62 | 30673 | 63 | EXTERNAL RAM 0
30668 | 63 | 30673 | 64 | EXTERNAL RAM 1
30668 | 64 | 30673 | 65 | LOST A/D CONVTR
30668 | 65 | 30673 | 66 | LOST DISPLAY
30668 | 66 | 30673 | 67 | LOST IO COMP
30668 | 67 | 30673 | 68 | LOST KEYPAD
30668 | 68 | 30673 | 69 | CFG FLASH PTR
30668 | 69 | 30673 | 70 | NETWORK ADDR CHG
30668 | 70 | 30673 | 71 | UPDATED FLASHCFG
30668 | 71 | 30673 | 72 | LOST A/D SHUTDWN
30668 | 72 | 30673 | 73 | CF CARD REMOVED
30668 | 73 | 30673 | 74 | CF CARD INSERTED
30668 | 74 | 30673 | 75 | CF INIT ERROR
30668 | 75 | 30673 | 76 | MCS-STAT OFFLINE
30668 | 76 | 30673 | 77 | BACnet Addr Chg
30668 | 77 | 30673 | 78 | FORCE MCS PROCOL
30668 | 78 | 30673 | 79 | UNUSED ALARM #78
30668 | 79 | 30673 | 80 | UNUSED ALARM #79
30668 | 80 | 30673 | 81 | CW OUT TRGT
30668 | 81 | 30673 | 82 | CTRL ZONE+
30668 | 82 | 30673 | 83 | CTRL ZONE-
30668 | 83 | 30673 | 84 | HGS TEMP ON
30668 | 84 | 30673 | 85 | HGS TEMP OFF
30668 | 85 | 30673 | 86 | HGS PSI ON
30668 | 86 | 30673 | 87 | HGS PSI OFF
30668 | 87 | 30673 | 88 | L. INJECT ON
30668 | 88 | 30673 | 89 | SUPERH TARGT
30668 | 89 | 30673 | 90 | SUPERH ZONE
30668 | 90 | 30673 | 91 | EXV LOAD ADJ
30668 | 91 | 30673 | 92 | EXV FINE ADJ
30668 | 92 | 30673 | 93 | EXV COURSE
30668 | 93 | 30673 | 94 | EXV Load DIV
30668 | 94 | 30673 | 95 | EXV MIN%
30668 | 95 | 30673 | 96 | EXV MAX%
30668 | 96 | 30673 | 97 | LO SUPERHEAT
30668 | 97 | 30673 | 98 | LOSUCTPSIDLY
30668 | 98 | 30673 | 99 | EXV DELAY
30668 | 99 | 30673 | 100 | EXV STRT TME
30668 | 100 | 30673 | 101 | MAX CW RESET
30668 | 101 | 30673 | 102 | LOW AMB. OFF
30668 | 102 | 30673 | 103 | POWERUP DLAY
30668 | 103 | 30673 | 104 | HI AMB. OFF
30668 | 104 | 30673 | 105 | STEP SENSIT
30668 | 105 | 30673 | 106 | STEP DELAY
30668 | 106 | 30673 | 107 | MAX ROC-
30668 | 107 | 30673 | 108 | MAX ROC+
30668 | 108 | 30673 | 109 | ROC INTERVAL
30668 | 109 | 30673 | 110 | MAX SLID %
30668 | 110 | 30673 | 111 | MIN SLID %
30668 | 111 | 30673 | 112 | MAX ADJUST %
30668 | 112 | 30673 | 113 | MIN ADJUST %
30668 | 113 | 30673 | 114 | SLIDE SENSIT
30668 | 114 | 30673 | 115 | AMP DB HI
30668 | 115 | 30673 | 116 | AMP DB LO
30668 | 116 | 30673 | 117 | LOAD PULSE
30668 | 117 | 30673 | 118 | UNLOAD PULSE
30668 | 118 | 30673 | 119 | LUBE OIL TMP
30668 | 119 | 30673 | 120 | LUBE OIL PSI
30668 | 120 | 30673 | 121 | LUBE DELAY
30668 | 121 | 30673 | 122 | HI WATER TMP
30668 | 122 | 30673 | 123 | C-PMPDWN FLA
30668 | 123 | 30673 | 124 | C-PMPDWN TMR
30668 | 124 | 30673 | 125 | CND STG1 ON
30668 | 125 | 30673 | 126 | CND STG1 OFF
30668 | 126 | 30673 | 127 | CND DIFF ON
30668 | 127 | 30673 | 128 | CND DIFF OFF
30668 | 128 | 30673 | 129 | CND MIN RUN
30668 | 129 | 30673 | 130 | CND VLV TARG
30668 | 130 | 30673 | 131 | CND START %
30668 | 131 | 30673 | 132 | CND VLV MIN
30668 | 132 | 30673 | 133 | CND VLV ROC-
30668 | 133 | 30673 | 134 | CND MIN SPD
30668 | 134 | 30673 | 135 | CND MAX SPD
30668 | 135 | 30673 | 136 | PULSE DELAY
30668 | 136 | 30673 | 137 | L-AMB ProcON
30668 | 137 | 30673 | 138 | CFG TEST=0
30668 | 138 | 30673 | 139 | A-CYC OFF-ON
30668 | 139 | 30673 | 140 | PMP DWN ON
30668 | 140 | 30673 | 141 | PMP DWN OFF
30668 | 141 | 30673 | 142 | PMP DWN DLAY
30668 | 142 | 30673 | 143 | A-CYC ON-ON
30668 | 143 | 30673 | 144 | COMP MIN RUN
30668 | 144 | 30673 | 145 | EXV ZONE X1
30668 | 145 | 30673 | 146 | EXV ZONE X2
30668 | 146 | 30673 | 147 | EXVroctmeIn1
30668 | 147 | 30673 | 148 | EXV rocZONE1
30668 | 148 | 30673 | 149 | EXV rocZONE2
30668 | 149 | 30673 | 150 | EXV rocZONE3
30668 | 150 | 30673 | 151 | EXV roc FAST
30668 | 151 | 30673 | 152 | EXV roc CHG
30668 | 152 | 30673 | 153 | PartWindDely
30668 | 153 | 30673 | 154 | OILPUMP OFF
30668 | 154 | 30673 | 155 | HI AMPS %
30668 | 155 | 30673 | 156 | LOampNoSTART
30668 | 156 | 30673 | 157 | LOW SUCTION
30668 | 157 | 30673 | 158 | LO SUCT UNLD
30668 | 158 | 30673 | 159 | LO SUCT RELD
30668 | 159 | 30673 | 160 | LOgas/LLsFLT
30668 | 160 | 30673 | 161 | HI DISC PSI
30668 | 161 | 30673 | 162 | HI DISC UNLD
30668 | 162 | 30673 | 163 | HI DISC RELD
30668 | 163 | 30673 | 164 | LO DiscSPRHT
30668 | 164 | 30673 | 165 | LO DISC PSI
30668 | 165 | 30673 | 166 | HiReturnTMP
30668 | 166 | 30673 | 167 | HI DISCH TMP
30668 | 167 | 30673 | 168 | DIS TMP UNLD
30668 | 168 | 30673 | 169 | DIS TMP RELD
30668 | 169 | 30673 | 170 | COND FAULT
30668 | 170 | 30673 | 171 | LOW OIL DIF
30668 | 171 | 30673 | 172 | UNSAFE OIL
30668 | 172 | 30673 | 173 | HIoilSealTmp
30668 | 173 | 30673 | 174 | Hi OIL TEMP
30668 | 174 | 30673 | 175 | SPPR Fault
30668 | 175 | 30673 | 176 | CompProof
30668 | 176 | 30673 | 177 | DIRTY FILTER
30668 | 177 | 30673 | 178 | LLS-ORIF-ON%
30668 | 178 | 30673 | 179 | ERCON ON%
30668 | 179 | 30673 | 180 | HIGHSumpTmp
30668 | 180 | 30673 | 181 | SafetyHold
30668 | 181 | 30673 | 182 | MAXCMP@MAX%
30668 | 182 | 30673 | 183 | LEAD COMP
30668 | 183 | 30673 | 184 | CMP ROTATION
30668 | 184 | 30673 | 185 | PUMP FAILURE
30668 | 185 | 30673 | 186 | LEAD PUMP
30668 | 186 | 30673 | 187 | DelyEconMech
30668 | 187 | 30673 | 188 | PMP OFF DLAY
30668 | 188 | 30673 | 189 | HI REF LVL
30668 | 189 | 30673 | 190 | LO REF LVL
30668 | 190 | 30673 | 191 | FREEZE
30668 | 191 | 30673 | 192 | NO STOP
30668 | 192 | 30673 | 193 | OilInjDiffTp
30668 | 193 | 30673 | 194 | Oil DiffTp
30668 | 194 | 30673 | 195 | EconVFDdel
30668 | 195 | 30673 | 196 | DEFon Temp
30668 | 196 | 30673 | 197 | DEFon Dela;y
30668 | 197 | 30673 | 198 | DEFon Cycle
30668 | 198 | 30673 | 199 | EcoOffsetON
30668 | 199 | 30673 | 200 | EconDelyFans
30668 | 200 | 30673 | 201 | EcoVlvMinVlv
30668 | 201 | 30673 | 202 | EcoVlvMaxVlv
30668 | 202 | 30673 | 203 | EcoVlvMaxAdj
30668 | 203 | 30673 | 204 | EcoVlvDelay
30668 | 204 | 30673 | 205 | EcoVlvMaxDly
30668 | 205 | 30673 | 206 | EcoVlv Mul
30668 | 206 | 30673 | 207 | EcoVlv Div
30668 | 207 | 30673 | 208 | Lost Leg Alm
30668 | 208 | 30673 | 209 | Reh On
30668 | 209 | 30673 | 210 | Reh Off adj
30668 | 210 | 30673 | 211 | Reh StrtDlay
30668 | 211 | 30673 | 212 | Reh Bld Dlay
30668 | 212 | 30673 | 213 | Reh Stg Dlay
30668 | 213 | 30673 | 214 | Barrel HtrOn
30668 | 214 | 30673 | 215 | Refig Leak
30668 | 215 | 30673 | 216 | Vi Pulse
30668 | 216 | 30673 | 217 | Vi Deadband
30668 | 217 | 30673 | 218 | Vi Delay
30668 | 218 | 30673 | 219 | low OilLevel
30668 | 219 | 30673 | 220 | HiDiscOffset
30668 | 220 | 30673 | 221 | 141
30668 | 221 | 30673 | 222 | ServiceMode
30668 | 222 | 30673 | 223 | Unload%
30668 | 223 | 30673 | 224 | Oil HeaterOn
30668 | 224 | 30673 | 225 | Oil CoolerOn
30668 | 225 | 30673 | 226 | Proc Target
30668 | 226 | 30673 | 227 | Proc Zone
30668 | 227 | 30673 | 228 | Proc Delay
30668 | 228 | 30673 | 229 | Proc Max ROC
30668 | 229 | 30673 | 230 | Proc MinSpd%
30668 | 230 | 30673 | 231 | Unloaded Off
30668 | 231 | 30673 | 232 | OverHeat
30668 | 232 | 30673 | 233 | SftyUnld Dly
30668 | 233 | 30673 | 234 | HGB Sfty Adj
30668 | 234 | 30673 | 235 | LO LIQ TMP
30668 | 235 | 30673 | 236 | LO LIQ UNLD
30668 | 236 | 30673 | 237 | HP LoSuctAdj
30668 | 237 | 30673 | 238 | DEF TRIG TMP
30668 | 238 | 30673 | 239 | DEF TRIG DEL
30668 | 239 | 30673 | 240 | DEFrevDelay
30668 | 240 | 30673 | 241 | DEF TERM TMP
30668 | 241 | 30673 | 242 | DEF TERMdely
30668 | 242 | 30673 | 243 | HP HEAT TARG
30668 | 243 | 30673 | 244 | HP CTL ZONE+
30668 | 244 | 30673 | 245 | HP CTL ZONE-
30668 | 245 | 30673 | 246 | PHASE LOSS
30668 | 246 | 30673 | 247 | PurgeAlarm
30668 | 247 | 30673 | 248 | Purge Count
30668 | 248 | 30673 | 249 | PurgePSIStrt
30668 | 249 | 30673 | 250 | ExcessPurge
30668 | 250 | 30673 | 251 | FLA COMP#1
30668 | 251 | 30673 | 252 | FLA COMP#2
30668 | 252 | 30673 | 253 | FLA COMP#3
30668 | 253 | 30673 | 254 | FLA COMP#4
30668 | 254 | 30673 | 255 | FLA COMP#5
30668 | 255 | 30673 | 256 | FLA COMP#6
30668 | 256 | 30673 | 257 | FLA COMP#7
30668 | 257 | 30673 | 258 | FLA COMP#8
30668 | 258 | 30673 | 259 | FLA COMP#9
30668 | 259 | 30673 | 260 | FLA COMP#10
30668 | 260 | 30673 | 261 | FLA COMP#11
30668 | 261 | 30673 | 262 | FLA COMP#12
30668 | 262 | 30673 | 263 | FLA COMP#13
30668 | 263 | 30673 | 264 | FLA COMP#14
30668 | 264 | 30673 | 265 | FLA COMP#15
30668 | 265 | 30673 | 266 | FLA COMP#16
30668 | 266 | 30673 | 267 | FLA COMP#17
30668 | 267 | 30673 | 268 | FLA COMP#18
30668 | 268 | 30673 | 269 | FLA COMP#19
30668 | 269 | 30673 | 270 | FLA COMP#20
30668 | 270 | 30673 | 271 | Temp Diff
30668 | 271 | 30673 | 272 | FRZ TempDiff
30668 | 272 | 30673 | 273 | PSI Diff
30668 | 273 | 30673 | 274 | Cond PSIDiff
30668 | 274 | 30673 | 275 | Low Voltage
30668 | 275 | 30673 | 276 | High Voltage
30668 | 276 | 30673 | 277 | ProcPmpLead
30668 | 277 | 30673 | 278 | ProcPmpFlt
30668 | 278 | 30673 | 279 | Not Used 199
30668 | 279 | 30673 | 280 | Not Used 200
30668 | 280 | 30673 | 281 | Not Used 201
30668 | 281 | 30673 | 282 | HI EVP DEL T
30668 | 282 | 30673 | 283 | HiSuctSheat
30668 | 283 | 30673 | 284 | Not Used 204
30668 | 284 | 30673 | 285 | MDP OIL DIFF
30668 | 285 | 30673 | 286 | Not Used 206
30668 | 286 | 30673 | 287 | Not Used 207
30668 | 287 | 30673 | 288 | Not Used 208
30668 | 288 | 30673 | 289 | Hi LWT-LQT
30668 | 289 | 30673 | 290 | Not Used 210
30668 | 290 | 30673 | 291 | Not Used 211
30668 | 291 | 30673 | 292 | Not Used 212
30668 | 292 | 30673 | 293 | Not Used 213
30668 | 293 | 30673 | 294 | Not Used 214
30668 | 294 | 30673 | 295 | TEST AO LO
30668 | 295 | 30673 | 296 | TEST AO HI
30668 | 296 | 30673 | 297 | LiqInj OnDis
30668 | 297 | 30673 | 298 | LiqInjOffDis
30668 | 298 | 30673 | 299 | LiqInj OnMtr
30668 | 299 | 30673 | 300 | LiqInjOffMtr
30668 | 300 | 30673 | 301 | Reserved 221
30668 | 301 | 30673 | 302 | Reserved 222
30668 | 302 | 30673 | 303 | Reserved 223
30668 | 303 | 30673 | 304 | Reserved 224
30668 | 304 | 30673 | 305 | Reserved 225
30668 | 305 | 30673 | 306 | Reserved 226
30668 | 306 | 30673 | 307 | Reserved 227
30668 | 307 | 30673 | 308 | Reserved 228
30668 | 308 | 30673 | 309 | Reserved 229
30668 | 309 | 30673 | 310 | Reserved 220
30668 | 310 | 30673 | 311 | Alarm SI SP1
30668 | 311 | 30673 | 312 | Alarm SI DP1
30668 | 312 | 30673 | 313 | Alarm SI ST1
30668 | 313 | 30673 | 314 | Spare
30668 | 314 | 30673 | 315 | Alarm SI AMPS1
30668 | 315 | 30673 | 316 | Alarm SI SPPR1
30668 | 316 | 30673 | 317 | Alarm SI WAT OUT
30668 | 317 | 30673 | 318 | Alarm SI WATER IN
30668 | 318 | 30673 | 319 | Alarm SI RUN/STOP
30668 | 319 | 30673 | 320 | Alarm SI DT1
30668 | 320 | 30673 | 321 | Alarm SI SPARE M-11
30668 | 321 | 30673 | 322 | Spare
30668 | 322 | 30673 | 323 | Alarm SI FLOW SW
30668 | 323 | 30673 | 324 | Alarm SI OIL LEVEL1
30668 | 324 | 30673 | 325 | Alarm SI SYS1 OFF
30668 | 325 | 30673 | 326 | Spare
30668 | 326 | 30673 | 327 | Alarm SI SP2
30668 | 327 | 30673 | 328 | Alarm SI DP2
30668 | 328 | 30673 | 329 | Alarm SI ST2
30668 | 329 | 30673 | 330 | Alarm SI DT2
30668 | 330 | 30673 | 331 | Alarm SI AMPS2
30668 | 331 | 30673 | 332 | Alarm SI OIL LEVEL2
30668 | 332 | 30673 | 333 | Alarm SI SPPR2
30668 | 333 | 30673 | 334 | Alarm SI SYS2 OFF
30668 | 334 | 30673 | 335 | Spare
30668 | 335 | 30673 | 336 | Alarm SI SPARE1-10
30668 | 336 | 30673 | 337 | Alarm SI SPARE1-11
30668 | 337 | 30673 | 338 | Alarm SI SPARE1-12
30668 | 338 | 30673 | 339 | Alarm SI SPARE1-13
30668 | 339 | 30673 | 340 | Alarm SI SPARE1-14
30668 | 340 | 30673 | 341 | Alarm SI SPARE1-15
30668 | 341 | 30673 | 342 | Alarm SI SPARE1-16
30668 | 342 | 30673 | 343 | Alarm SI BMS RUN
30668 | 343 | 30673 | 344 | Alarm SI SSH 1
30668 | 344 | 30673 | 345 | Alarm SI SSH 2
30668 | 345 | 30673 | 346 | Alarm SI SPARE2-4
30668 | 346 | 30673 | 347 | Alarm SI SPARE2-5
30668 | 347 | 30673 | 348 | Alarm SI SPARE2-6
30668 | 348 | 30673 | 349 | Alarm SI SPARE2-7
30668 | 349 | 30673 | 350 | Alarm SI SPARE2-8
30668 | 350 | 30673 | 351 | Alarm SI SPARE2-9
30668 | 351 | 30673 | 352 | Alarm SI SPARE2-10
30668 | 352 | 30673 | 353 | Alarm SI SPARE2-11
30668 | 353 | 30673 | 354 | Alarm SI SPARE2-12
30668 | 354 | 30673 | 355 | Alarm SI SPARE2-13
30668 | 355 | 30673 | 356 | Alarm SI SPARE2-14
30668 | 356 | 30673 | 357 | Alarm SI SPARE2-15
30668 | 357 | 30673 | 358 | Alarm SI SPARE2-16
30668 | 358 | 30673 | 359 | Alarm SI SPARE3-1
30668 | 359 | 30673 | 360 | Alarm SI SPARE3-2
30668 | 360 | 30673 | 361 | Alarm SI SPARE3-3
30668 | 361 | 30673 | 362 | Alarm SI SPARE3-4
30668 | 362 | 30673 | 363 | Alarm SI SPARE3-5
30668 | 363 | 30673 | 364 | Alarm SI SPARE3-6
30668 | 364 | 30673 | 365 | Alarm SI SPARE3-7
30668 | 365 | 30673 | 366 | Alarm SI SPARE3-8
30668 | 366 | 30673 | 367 | Alarm SI SPARE3-9
30668 | 367 | 30673 | 368 | Alarm SI SPARE3-10
30668 | 368 | 30673 | 369 | Alarm SI SPARE3-11
30668 | 369 | 30673 | 370 | Alarm SI SPARE3-12
30668 | 370 | 30673 | 371 | Alarm SI SPARE3-13
30668 | 371 | 30673 | 372 | Alarm SI SPARE3-14
30668 | 372 | 30673 | 373 | Alarm SI SPARE3-15
30668 | 373 | 30673 | 374 | Alarm SI SPARE3-16
30668 | 374 | 30673 | 375 | Alarm SI SPARE4-1
30668 | 375 | 30673 | 376 | Alarm SI SPARE4-2
30668 | 376 | 30673 | 377 | Alarm SI SPARE4-3
30668 | 377 | 30673 | 378 | Alarm SI SPARE4-4
30668 | 378 | 30673 | 379 | Alarm SI SPARE4-5
30668 | 379 | 30673 | 380 | Alarm SI SPARE4-6
30668 | 380 | 30673 | 381 | Alarm SI SPARE4-7
30668 | 381 | 30673 | 382 | Alarm SI SPARE4-8
30668 | 382 | 30673 | 383 | Alarm SI SPARE4-9
30668 | 383 | 30673 | 384 | Alarm SI SPARE4-10
30668 | 384 | 30673 | 385 | Alarm SI SPARE4-11
30668 | 385 | 30673 | 386 | Alarm SI SPARE4-12
30668 | 386 | 30673 | 387 | Alarm SI SPARE4-13
30668 | 387 | 30673 | 388 | Alarm SI SPARE4-14
30668 | 388 | 30673 | 389 | Alarm SI SPARE4-15
30668 | 389 | 30673 | 390 | Alarm SI SPARE4-16
30668 | 390 | 30673 | 391 | Alarm SI SPARE5-1
30668 | 391 | 30673 | 392 | Alarm SI SPARE5-2
30668 | 392 | 30673 | 393 | Alarm SI SPARE5-3
30668 | 393 | 30673 | 394 | Alarm SI SPARE5-4
30668 | 394 | 30673 | 395 | Alarm SI SPARE5-5
30668 | 395 | 30673 | 396 | Alarm SI SPARE5-6
30668 | 396 | 30673 | 397 | Alarm SI SPARE5-7
30668 | 397 | 30673 | 398 | Alarm SI SPARE5-8
30668 | 398 | 30673 | 399 | Alarm SI SPARE5-9
30668 | 399 | 30673 | 400 | Alarm SI SPARE5-10
30668 | 400 | 30673 | 401 | Alarm SI SPARE5-11
30668 | 401 | 30673 | 402 | Alarm SI SPARE5-12
30668 | 402 | 30673 | 403 | Alarm SI SPARE5-13
30668 | 403 | 30673 | 404 | Alarm SI SPARE5-14
30668 | 404 | 30673 | 405 | Alarm SI SPARE5-15
30668 | 405 | 30673 | 406 | Alarm SI SPARE5-16
30668 | 406 | 30673 | 407 | Alarm SI SPARE6-1
30668 | 407 | 30673 | 408 | Alarm SI SPARE6-2
30668 | 408 | 30673 | 409 | Alarm SI SPARE6-3
30668 | 409 | 30673 | 410 | Alarm SI SPARE6-4
30668 | 410 | 30673 | 411 | Alarm SI SPARE6-5
30668 | 411 | 30673 | 412 | Alarm SI SPARE6-6
30668 | 412 | 30673 | 413 | Alarm SI SPARE6-7
30668 | 413 | 30673 | 414 | Alarm SI SPARE6-8
30668 | 414 | 30673 | 415 | Alarm SI SPARE6-9
30668 | 415 | 30673 | 416 | Alarm SI SPARE6-10
30668 | 416 | 30673 | 417 | Alarm SI SPARE6-11
30668 | 417 | 30673 | 418 | Alarm SI SPARE6-12
30668 | 418 | 30673 | 419 | Alarm SI SPARE6-13
30668 | 419 | 30673 | 420 | Alarm SI SPARE6-14
30668 | 420 | 30673 | 421 | Alarm SI SPARE6-15
30668 | 421 | 30673 | 422 | Alarm SI SPARE6-16
30668 | 422 | 30673 | 423 | BadPoint-SI ALM
30668 | 423 | 30673 | 424 | Alarm RO SYS1 CMP M
30668 | 424 | 30673 | 425 | Alarm RO SYS1 CMP P
30668 | 425 | 30673 | 426 | Alarm RO SYS1 CR4
30668 | 426 | 30673 | 427 | Alarm RO SYS1 CR3
30668 | 427 | 30673 | 428 | Alarm RO SYS1 L INJ
30668 | 428 | 30673 | 429 | Alarm RO SYS1 ECO
30668 | 429 | 30673 | 430 | Alarm RO HGBP 1
30668 | 430 | 30673 | 431 | Alarm RO ALARM
30668 | 431 | 30673 | 432 | Alarm RO SYS1 FANs1
30668 | 432 | 30673 | 433 | Alarm RO SYS1 FANs2
30668 | 433 | 30673 | 434 | Alarm RO SYS2 CMP M
30668 | 434 | 30673 | 435 | Alarm RO SYS2 CMP P
30668 | 435 | 30673 | 436 | Alarm RO SYS2 CR4
30668 | 436 | 30673 | 437 | Alarm RO SYS2 CR3
30668 | 437 | 30673 | 438 | Alarm RO SYS2 ECO
30668 | 438 | 30673 | 439 | Alarm RO SYS2 FANs3
30668 | 439 | 30673 | 440 | Alarm RO SYS2 FANs4
30668 | 440 | 30673 | 441 | Alarm RO HGBP 2
30668 | 441 | 30673 | 442 | Alarm RO SPARE1-9
30668 | 442 | 30673 | 443 | Alarm RO SPARE1-10
30668 | 443 | 30673 | 444 | Alarm RO SPARE2-1
30668 | 444 | 30673 | 445 | Alarm RO SPARE2-2
30668 | 445 | 30673 | 446 | Alarm RO SPARE2-3
30668 | 446 | 30673 | 447 | Alarm RO SPARE2-4
30668 | 447 | 30673 | 448 | Alarm RO SPARE2-5
30668 | 448 | 30673 | 449 | Alarm RO SPARE2-6
30668 | 449 | 30673 | 450 | Alarm RO SPARE2-7
30668 | 450 | 30673 | 451 | Alarm RO SPARE2-8
30668 | 451 | 30673 | 452 | Alarm RO SPARE2-9
30668 | 452 | 30673 | 453 | Alarm RO SPARE2-10
30668 | 453 | 30673 | 454 | Alarm RO SPARE3-1
30668 | 454 | 30673 | 455 | Alarm RO SPARE3-2
30668 | 455 | 30673 | 456 | Alarm RO SPARE3-3
30668 | 456 | 30673 | 457 | Alarm RO SPARE3-4
30668 | 457 | 30673 | 458 | Alarm RO SPARE3-5
30668 | 458 | 30673 | 459 | Alarm RO SPARE3-6
30668 | 459 | 30673 | 460 | Alarm RO SPARE3-7
30668 | 460 | 30673 | 461 | Alarm RO SPARE3-8
30668 | 461 | 30673 | 462 | Alarm RO SPARE3-9
30668 | 462 | 30673 | 463 | Alarm RO SPARE3-10
30668 | 463 | 30673 | 464 | Alarm RO SPARE4-1
30668 | 464 | 30673 | 465 | Alarm RO SPARE4-2
30668 | 465 | 30673 | 466 | Alarm RO SPARE4-3
30668 | 466 | 30673 | 467 | Alarm RO SPARE4-4
30668 | 467 | 30673 | 468 | Alarm RO SPARE4-5
30668 | 468 | 30673 | 469 | Alarm RO SPARE4-6
30668 | 469 | 30673 | 470 | Alarm RO SPARE4-7
30668 | 470 | 30673 | 471 | Alarm RO SPARE4-8
30668 | 471 | 30673 | 472 | Alarm RO SPARE4-9
30668 | 472 | 30673 | 473 | Alarm RO SPARE4-10
30668 | 473 | 30673 | 474 | Alarm RO SPARE5-1
30668 | 474 | 30673 | 475 | Alarm RO SPARE5-2
30668 | 475 | 30673 | 476 | Alarm RO SPARE5-3
30668 | 476 | 30673 | 477 | Alarm RO SPARE5-4
30668 | 477 | 30673 | 478 | Alarm RO SPARE5-5
30668 | 478 | 30673 | 479 | Alarm RO SPARE5-6
30668 | 479 | 30673 | 480 | Alarm RO SPARE5-7
30668 | 480 | 30673 | 481 | Alarm RO SPARE5-8
30668 | 481 | 30673 | 482 | Alarm RO SPARE5-9
30668 | 482 | 30673 | 483 | Alarm RO SPARE5-10
30668 | 483 | 30673 | 484 | Alarm RO SPARE6-1
30668 | 484 | 30673 | 485 | Alarm RO SPARE6-2
30668 | 485 | 30673 | 486 | Alarm RO SPARE6-3
30668 | 486 | 30673 | 487 | Alarm RO SPARE6-4
30668 | 487 | 30673 | 488 | Alarm RO SPARE6-5
30668 | 488 | 30673 | 489 | Alarm RO SPARE6-6
30668 | 489 | 30673 | 490 | Alarm RO SPARE6-7
30668 | 490 | 30673 | 491 | Alarm RO SPARE6-8
30668 | 491 | 30673 | 492 | Alarm RO SPARE6-9
30668 | 492 | 30673 | 493 | Alarm RO SPARE6-10
30668 | 493 | 30673 | 494 | Alarm RO SPARE7-1
30668 | 494 | 30673 | 495 | Alarm RO SPARE7-2
30668 | 495 | 30673 | 496 | Alarm RO SPARE7-3
30668 | 496 | 30673 | 497 | Alarm RO SPARE7-4
30668 | 497 | 30673 | 498 | Alarm RO SPARE7-5
30668 | 498 | 30673 | 499 | Alarm RO SPARE7-6
30668 | 499 | 30673 | 500 | Alarm RO SPARE7-7
30668 | 500 | 30673 | 501 | Alarm RO SPARE7-8
30668 | 501 | 30673 | 502 | Alarm RO SPARE7-9
30668 | 502 | 30673 | 503 | Alarm RO SPARE7-10
30668 | 503 | 30673 | 504 | BadPoint-RO ALM
30668 | 504 | 30673 | 505 | ALARM IS NOT ACTIVE
30668 | 505 | 30673 | 506 | SETPOINT-231
30668 | 506 | 30673 | 507 | SETPOINT-232
30668 | 507 | 30673 | 508 | SETPOINT-233
30668 | 508 | 30673 | 509 | SETPOINT-234
30668 | 509 | 30673 | 510 | SETPOINT-235
30668 | 510 | 30673 | 511 | SETPOINT-236
30668 | 511 | 30673 | 512 | SETPOINT-237
30668 | 512 | 30673 | 513 | SETPOINT-238
30668 | 513 | 30673 | 514 | SETPOINT-239
30668 | 514 | 30673 | 515 | SETPOINT-240
30668 | 515 | 30673 | 516 | SETPOINT-241
30668 | 516 | 30673 | 517 | SETPOINT-242
30668 | 517 | 30673 | 518 | SETPOINT-243
30668 | 518 | 30673 | 519 | SETPOINT-244
30668 | 519 | 30673 | 520 | SETPOINT-245
30668 | 520 | 30673 | 521 | SETPOINT-246
30668 | 521 | 30673 | 522 | SETPOINT-247
30668 | 522 | 30673 | 523 | SETPOINT-248
30668 | 523 | 30673 | 524 | SETPOINT-249
30668 | 524 | 30673 | 525 | SETPOINT-250
30668 | 525 | 30673 | 526 | SETPOINT-251
30668 | 526 | 30673 | 527 | SETPOINT-252
30668 | 527 | 30673 | 528 | SETPOINT-253
30668 | 528 | 30673 | 529 | SETPOINT-254
30668 | 529 | 30673 | 530 | SETPOINT-255
30668 | 530 | 30673 | 531 | BRAKE CHECK
30668 | 531 | 30673 | 532 | POWER CARD TEMP
30668 | 532 | 30673 | 533 | EARTH FAULT
30668 | 533 | 30673 | 534 | CTRL CARD TEMP
30668 | 534 | 30673 | 535 | CTRL WORD TO
30668 | 535 | 30673 | 536 | OVER CURRENT
30668 | 536 | 30673 | 537 | TORQUE LIMIT
30668 | 537 | 30673 | 538 | MOTOR TH OVER
30668 | 538 | 30673 | 539 | MOTOR ETR OVER
30668 | 539 | 30673 | 540 | INVERTER OVERLD
30668 | 540 | 30673 | 541 | DC UNDER VOLT
30668 | 541 | 30673 | 542 | DC OVER VOLT
30668 | 542 | 30673 | 543 | SHORT CIRCUIT
30668 | 543 | 30673 | 544 | INRUSH FAULT
30668 | 544 | 30673 | 545 | MAIN PHASE LOSS
30668 | 545 | 30673 | 546 | AMA NOT OK
30668 | 546 | 30673 | 547 | LIVE ZERO ERROR
30668 | 547 | 30673 | 548 | INTERNAL FAULT
30668 | 548 | 30673 | 549 | BRAKE OVERLOAD
30668 | 549 | 30673 | 550 | U PHASE LOSS
30668 | 550 | 30673 | 551 | V PHASE LOSS
30668 | 551 | 30673 | 552 | W PHASE LOSS
30668 | 552 | 30673 | 553 | FIELDBUS FAULT
30668 | 553 | 30673 | 554 | 24V SUPPLY LOW
30668 | 554 | 30673 | 555 | MAINS FAILURE
30668 | 555 | 30673 | 556 | 1.8V SUPPLY LOW
30668 | 556 | 30673 | 557 | BRAKE RESISTOR
30668 | 557 | 30673 | 558 | BRAKE IGBT
30668 | 558 | 30673 | 559 | OPTION CHANGE
30668 | 559 | 30673 | 560 | DRIVE INIT
30668 | 560 | 30673 | 561 | SAFE STOP
30668 | 561 | 30673 | 562 | MECH BRAKE LOW
30668 | 562 | 30673 | 563 | SERIAL TIMEOUT
30668 | 563 | 30673 | 564 | MAINS FAILURE
30668 | 564 | 30673 | 565 | ENVELOPE FAULT
30668 | 565 | 30673 | 566 | ENVELOP INIT FLT
30668 | 566 | 30673 | 567 | COMP SHORT CYCLE
30668 | 567 | 30673 | 568 | HIGH OIL TEMP
30668 | 568 | 30673 | 569 | LOW OIL LEVEL
30668 | 569 | 30673 | 570 | UNUSED
30668 | 570 | 30673 | 571 | MOTOR OVERLOAD
30668 | 571 | 30673 | 572 | WRONG PHASE SEQ
30668 | 572 | 30673 | 573 | MTR THERML OVRLD
30668 | 573 | 30673 | 574 | INVERTER FAULT
30668 | 574 | 30673 | 575 | OVER CURRENT
30668 | 575 | 30673 | 576 | OVER VOLTAGE
30668 | 576 | 30673 | 577 | UNDER VOLTAGE
30668 | 577 | 30673 | 578 | FC OVER TEMP
30668 | 578 | 30673 | 579 | HW CONFIG FAULT
30668 | 579 | 30673 | 580 | PWR DATA CFG FLT
30668 | 580 | 30673 | 581 | MTR DATA CFG FLT
30668 | 581 | 30673 | 582 | HARDWARE FAULT
30668 | 582 | 30673 | 583 | UNUSED
30668 | 583 | 30673 | 584 | TEMP SENSOR FLT
30668 | 584 | 30673 | 585 | UNUSED
30668 | 585 | 30673 | 586 | UNUSED
30668 | 586 | 30673 | 587 | UNUSED
30668 | 587 | 30673 | 588 | UNUSED
30668 | 588 | 30673 | 589 | UNUSED
30668 | 589 | 30673 | 590 | UNUSED
30668 | 590 | 30673 | 591 | UNUSED
30668 | 591 | 30673 | 592 | UNUSED
30668 | 592 | 30673 | 593 | UNUSED
30668 | 593 | 30673 | 594 | UNUSED
30668 | 594 | 30673 | 595 | CHILLER OFFLINE
30758 | 0 |  | 1 | CHILLER MODE
30758 | 1 |  | 2 | ICE MAKING MODE
30758 | 2 |  | 3 | HEATING MODE
BMS Number | BMS ID
1 | 1
2 | 2