## LCW-0500VC2IOLOS
Controller Type | Device Type
LCW-0500VC2IOLOS ( Reliance Industries DYI00001) | CHILLER
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
OIL PUMP Relay | 01 | 00002 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Oil Heater 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Liquid Injection Solenoid Valve 1 Relay | 01 | 00004 | 01 | 9600 | Relay-Outputs | 4 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Oil Heater 2 Relay | 01 | 00006 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
REF HTR Relay | 01 | 00007 | 01 | 9600 | Relay-Outputs | 6 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor VFD Run Relay | 01 | 00011 | 01 | 9600 | Relay-Outputs | 7 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
REF Leak Relay | 01 | 00048 | 01 | 9600 | Relay-Outputs | 8 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
REF FLDBCK Relay | 01 | 00049 | 01 | 9600 | Relay-Outputs | 9 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Suction Pressure 1 | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Discharge Pressure 1 | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Oil Pressure P1 | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Oil Pressure P2 | 04 | 30004 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Oil Pressure P3 | 04 | 30005 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Cooler Water In Temp | 04 | 30006 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Water Out Temp | 04 | 30007 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Condenser Water In Temp | 04 | 30008 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Condenser Water Out Temp | 04 | 30009 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
FLSH T LV% | 04 | 30010 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
IGV 1 % | 04 | 30011 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Oil Temp 1 | 04 | 30012 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Flow Switch | 04 | 30013 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | status | Yes
Condenser Flow Switch | 04 | 30014 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | status | Yes
Unit Switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | status | Yes
VFD Alarm 1 | 04 | 30016 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | status | Yes
CMD Freq 1 | 04 | 30023 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hz
Cap Temp 1 | 04 | 30024 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Power KW1 | 04 | 30025 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | kW
MtrVoltage1 | 04 | 30026 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | V
Frequency1 | 04 | 30027 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | Hz
MtrAmps1 | 04 | 30028 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
MtrRPM1 | 04 | 30029 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 10 | DECIMAL | Periodic | Yes |  |  |  | rpm
DCVoltage1 | 04 | 30030 | 01 | 9600 | Analog-Inputs | 20 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | V
HeatSnkTmp1 | 04 | 30031 | 01 | 9600 | Analog-Inputs | 21 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Suction Temperature 1 | 04 | 30033 | 01 | 9600 | Analog-Inputs | 22 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Discharge Temperature 1 | 04 | 30034 | 01 | 9600 | Analog-Inputs | 23 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Eco Pr | 04 | 30035 | 01 | 9600 | Analog-Inputs | 24 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Eco Tmp | 04 | 30036 | 01 | 9600 | Analog-Inputs | 25 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MotorT O11 | 04 | 30037 | 01 | 9600 | Analog-Inputs | 26 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MotorT O12 | 04 | 30038 | 01 | 9600 | Analog-Inputs | 27 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MotorT O21 | 04 | 30039 | 01 | 9600 | Analog-Inputs | 28 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MotorT O22 | 04 | 30040 | 01 | 9600 | Analog-Inputs | 29 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Oil Cool T | 04 | 30041 | 01 | 9600 | Analog-Inputs | 30 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Liquid Temp SC | 04 | 30042 | 01 | 9600 | Analog-Inputs | 31 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
FlsTnkLvl | 04 | 30043 | 01 | 9600 | Digital-Inputs | 5 |  | 4 | 1 | DECIMAL | status | Yes
SPPR 1 | 04 | 30044 | 01 | 9600 | Digital-Inputs | 6 |  | 4 | 1 | DECIMAL | status | Yes
Liquid Temp 1 | 04 | 30045 | 01 | 9600 | Analog-Inputs | 32 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
P11 | 04 | 30046 | 01 | 9600 | Analog-Inputs | 33 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
IGV 2 % | 04 | 30047 | 01 | 9600 | Analog-Inputs | 34 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Liquid PR | 04 | 30048 | 01 | 9600 | Analog-Inputs | 35 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
HGB On | 04 | 30050 | 01 | 9600 | Analog-Inputs | 36 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
HGB Off | 04 | 30051 | 01 | 9600 | Analog-Inputs | 37 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
HGBEXVF | 04 | 30052 | 01 | 9600 | Analog-Inputs | 38 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
HGB UL | 04 | 30053 | 01 | 9600 | Analog-Inputs | 38 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | %
Max Speed | 04 | 30054 | 01 | 9600 | Analog-Inputs | 39 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | %
Oil Pressure Diff | 04 | 30055 | 01 | 9600 | Analog-Inputs | 40 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Surge Frequency 1 | 04 | 30059 | 01 | 9600 | Analog-Inputs | 41 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | Hz
RPM Diff 1 | 04 | 30060 | 01 | 9600 | Analog-Inputs | 42 |  | 4 | 0.1 | DECIMAL | Periodic | Yes
Comp Surge 1 | 04 | 30061 | 01 | 9600 | Digital-Inputs | 9 |  | 4 | 1 | DECIMAL | Status | Yes
MaxFreqDV | 04 | 30062 | 01 | 9600 | Analog-Inputs | 43 |  | 4 | 0.1 | DECIMAL | Periodic | Yes
IGV2 DIFF | 04 | 30063 | 01 | 9600 | Analog-Inputs |  |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
IGV2 FLT | 04 | 30064 | 01 | 9600 | Digital-Inputs |  |  | 4 | 1 | DECIMAL | status | Yes
DIS-OIL 1 | 04 | 30069 | 01 | 9600 | Analog-Inputs | 44 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Evaporator Approach 1 | 04 | 30071 | 01 | 9600 | Analog-Inputs | 45 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
DP1 Absolut | 04 | 30072 | 01 | 9600 | Analog-Inputs | 46 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIA
SP1 Absolut | 04 | 30073 | 01 | 9600 | Analog-Inputs | 47 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIA
EvpCndFlw | 04 | 30074 | 01 | 9600 | Digital-Inputs | 7 |  | 4 | 1 | DECIMAL | status | Yes
VaneClosed | 04 | 30075 | 01 | 9600 | Digital-Inputs | 8 |  | 4 | 1 | DECIMAL | status | Yes
MtrTmpH1 | 04 | 30076 | 01 | 9600 | Analog-Inputs | 48 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MtrTmpH2 | 04 | 30077 | 01 | 9600 | Analog-Inputs | 49 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
MtrTmpH3 | 04 | 30078 | 01 | 9600 | Analog-Inputs | 50 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
OC TmpHi | 04 | 30079 | 01 | 9600 | Digital-Inputs | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes
OC TmpLo | 04 | 30080 | 01 | 9600 | Digital-Inputs | 10 |  | 4 | 1 | DECIMAL | Periodic | Yes
OC Hi/Lo | 04 | 30081 | 01 | 9600 | Digital-Inputs | 11 |  | 4 | 1 | DECIMAL | Periodic | Yes
PSI ratio | 04 | 30082 | 01 | 9600 | Analog-Inputs | 51 |  | 4 | 0.1 | DECIMAL | Periodic | Yes
Lockout Reset | 04 | 30083 | 01 | 9600 | Digital-Inputs | 12 |  | 4 | 1 | DECIMAL | status | Yes
EVA APPRO 1 | 04 | 30084 | 01 | 9600 | Analog-Inputs | 52 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 0 | 5 | F
Condenser Approach | 04 | 30085 | 01 | 9600 | Analog-Inputs | 53 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Comp 1 vane | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Stage 2 EXV | 04 | 30202 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Stage 1 EXV | 04 | 30203 | 01 | 9600 | Analog-Outputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
HGB 1 | 04 | 30204 | 01 | 9600 | Analog-Outputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
CmpSpeed%M | 04 | 30205 | 01 | 9600 | Analog-Outputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Start 1 | 04 | 30206 | 01 | 9600 | Analog-Outputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Oil CL EXV | 04 | 30209 | 01 | 9600 | Analog-Outputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Loading%1 | 04 | 30210 | 01 | 9600 | Analog-Outputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 2 vane | 04 | 30201 | 01 | 9600 | Analog-Outputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Unit State | 04 | 30306 | 01 | 9600 | Control-Information | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps Delay | 04 | 30317 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 1 FLA | 04 | 30319 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp 1 | 04 | 30327 | 01 | 9600 | Analog-Inputs | 54 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Suction Superheat 1 | 04 | 30328 | 01 | 9600 | Analog-Inputs | 55 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Saturated Discharge Temp 1 | 04 | 30329 | 01 | 9600 | Analog-Inputs | 56 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Discharge Superheat 1 | 04 | 30330 | 01 | 9600 | Analog-Inputs | 57 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Oil Pressure Diff 1 | 04 | 30375 | 01 | 9600 | Analog-Inputs | 58 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | status | Yes
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | status | Yes
RH Compressor 1 On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH OIL PUMP | 04 | 30679 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH Oil Heater 1 | 04 | 30680 | 01 | 9600 | Runhours | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH Liquid Injection Solenoid Valve 1 | 04 | 30681 | 01 | 9600 | Runhours | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH Oil Heater 2 | 04 | 30683 | 01 | 9600 | Runhours | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH REF HTR | 04 | 30684 | 01 | 9600 | Runhours | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH Compressor VFD Run | 04 | 30688 | 01 | 9600 | Runhours | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH REF Leak | 04 | 30725 | 01 | 9600 | Runhours | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
RH REF FLDBCK | 04 | 30726 | 01 | 9600 | Runhours | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | hrs
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
Liquid Injection On | 03 | 40308 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Approach Tar | 03 | 40309 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LvlZone+- | 03 | 40310 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV LOAD DIV | 03 | 40314 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV MAX | 03 | 40316 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX CW RESET | 03 | 40321 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX ADJUST | 03 | 40332 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST | 03 | 40333 | 01 | 9600 | Setpoints | 26 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
Vane SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 27 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
VANEOpnPulse | 03 | 40337 | 01 | 9600 | Setpoints | 28 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
VANEClsPulse | 03 | 40338 | 01 | 9600 | Setpoints | 29 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
Low Oil Temp | 03 | 40339 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LUBE OIL PSI | 03 | 40340 | 01 | 9600 | Setpoints | 31 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LUBE DELAY | 03 | 40341 | 01 | 9600 | Setpoints | 32 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
CmpOff Vane% | 03 | 40343 | 01 | 9600 | Setpoints | 33 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CmpOff Delay | 03 | 40344 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
PostLubeDely | 03 | 40362 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | min
OILPUMP OFF | 03 | 40374 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI AMPS | 03 | 40375 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO Disc SPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 50 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO DISC PSI | 03 | 40385 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 52 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 53 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LOW OIL DIF | 03 | 40391 | 01 | 9600 | Setpoints | 55 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
UNSAFE OIL | 03 | 40392 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HIOilFeedTmp | 03 | 40393 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI OIL TEMP | 03 | 40394 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI Motor TMP | 03 | 40395 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Surge Trip | 03 | 40396 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | rpm
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
RefLvlExvAdj | 03 | 40410 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CmpMinSpeed% | 03 | 40428 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CmpMaxSpeed% | 03 | 40429 | 01 | 9600 | Setpoints | 65 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CmpSpdUnld% | 03 | 40430 | 01 | 9600 | Setpoints | 66 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CmpSpdLoad% | 03 | 40431 | 01 | 9600 | Setpoints | 67 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MinLiftTemp | 03 | 40432 | 01 | 9600 | Setpoints | 68 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
MaxLiftTemp | 03 | 40433 | 01 | 9600 | Setpoints | 69 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Barrel HtrOn | 03 | 40434 | 01 | 9600 | Setpoints | 70 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
IGV2 FLTS | 03 | 40435 | 01 | 9600 | Setpoints | 71 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
Hi Sbclr Lvl | 03 | 40439 | 01 | 9600 | Setpoints | 72 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
OilHeaterON | 03 | 40444 | 01 | 9600 | Setpoints | 73 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Oil CoolerOn | 03 | 40445 | 01 | 9600 | Setpoints | 74 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Unloaded Off | 03 | 40451 | 01 | 9600 | Setpoints | 75 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO LIQ TMP | 03 | 40455 | 01 | 9600 | Setpoints | 76 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO LIQ UNLD | 03 | 40456 | 01 | 9600 | Setpoints | 77 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
PHASE LOSS | 03 | 40466 | 01 | 9600 | Setpoints | 78 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | min
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 79 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
SPD OPTIMIZE | 03 | 40488 | 01 | 9600 | Setpoints | 80 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 81 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
COMP SURGING | 03 | 40509 | 01 | 9600 | Setpoints | 82 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | C
AMP SurgeROC | 03 | 40510 | 01 | 9600 | Setpoints | 83 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
LiftSurgeROC | 03 | 40511 | 01 | 9600 | Setpoints | 84 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
SurgingCount | 03 | 40512 | 01 | 9600 | Setpoints | 85 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | C
SurgingTime | 03 | 40513 | 01 | 9600 | Setpoints | 86 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
Lo/Hi OC Tmp | 03 | 40514 | 01 | 9600 | Setpoints | 87 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
VFD Fault | 03 | 40515 | 01 | 9600 | Setpoints | 88 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
High VFD Temp | 03 | 40516 | 01 | 9600 | Setpoints | 89 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
VFD Unld/Reld | 03 | 40517 | 01 | 9600 | Setpoints | 90 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint