## LCWX1-0425FI
Controller Type | Device Type
LCWX1-0425FI (Rajarajeshwari Memorial Hospital 9812-A-L14) | CHILLER
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 1 Relay | 01 | 00004 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Suction Pressure 1 | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 25 | 70 | PSIG
Discharge Pressure 1 | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 149 | PSIG
Oil Pressure 1 | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 95 | 145 | PSIG
Cooler Water Out Temp | 04 | 30004 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 39 | 75 | F
Cooler Water In Temp | 04 | 30005 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 44 | 85 | F
Compressor 1 Current | 04 | 30006 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Suction Temperature 1 | 04 | 30007 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Discharge Temperature 1 | 04 | 30008 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 149 | F
REF LVL1 | 04 | 30009 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 11 | 60 | %
PT1000 1 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 65 | 130 | F
Condenser Water In Temp | 04 | 30011 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 50 | 100 | F
Liquid Temp 1 | 04 | 30012 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 32 | 65 | F
Flow Switch 1 | 04 | 30013 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Oil level switch 1 | 04 | 30014 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Unit Switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | Status | Yes
SPPR 1 | 04 | 30016 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | Status | Yes
DIS-OIL 1 | 04 | 30017 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes
VrOilFlow1 | 04 | 30018 | 01 | 9600 | Digital-Inputs | 5 |  | 4 | 1 | DECIMAL | Status | Yes
BMS RUN | 04 | 30019 | 01 | 9600 | Digital-Inputs | 6 |  | 4 | 1 | DECIMAL | Status | Yes
SSH 1 | 04 | 30020 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes
Electronic Expansion Valve 1 | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
CND VALV | 04 | 30203 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Chiller State | 04 | 30306 | 01 | 9600 | Control-Information | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps Delay | 04 | 30317 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 1 FLA | 04 | 30319 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp 1 | 04 | 30327 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Suction Superheat 1 | 04 | 30328 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 0 | 12 | F
Saturated Discharge Temp 1 | 04 | 30329 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Discharge Superheat | 04 | 30330 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 26 | F
Oil Pressure Diff | 04 | 30375 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | Status | Yes
RH Compressor 1 On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Load Solenoid Valve 1 | 04 | 30680 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Unload Solenoid Valve 1 | 04 | 30681 | 01 | 9600 | Runhours | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
REF LVL TARG | 03 | 40309 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
REF LVL ZONE | 03 | 40310 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV Load DIV | 03 | 40314 | 01 | 9600 | Setpoints | 9 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV MAX | 03 | 40316 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 12 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 13 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 14 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 15 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 16 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 17 |  | 4 | 1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | sec.
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 20 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
MAX SLID | 03 | 40330 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN SLIDE % | 03 | 40331 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MAX ADJUST | 03 | 40332 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST | 03 | 40333 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
SLIDE SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 25 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint
LOAD PULSE | 03 | 40337 | 01 | 9600 | Setpoints | 26 |  | 4 | 1 | DECIMALSIGNED | Periodic | No | Setpoint
UNLOAD PULSE | 03 | 40338 | 01 | 9600 | Setpoints | 27 |  | 4 | 1 | DECIMALSIGNED | Periodic | No | Setpoint
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 28 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC OFF-ON | 03 | 40359 | 01 | 9600 | Setpoints | 29 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
PMP DWN OFF | 03 | 40361 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
PMP DWN DLAY | 03 | 40362 | 01 | 9600 | Setpoints | 31 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
A-CYC ON-ON | 03 | 40363 | 01 | 9600 | Setpoints | 32 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 33 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | min.
HI AMPS | 03 | 40375 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 36 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 38 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO Disc SPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LOW OIL DIF | 03 | 40391 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
UNSAFE OIL | 03 | 40392 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI Motor TMP | 03 | 40394 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
SPPR Fault | 03 | 40395 | 01 | 9600 | Setpoints | 50 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint
DIRTY FILTER | 03 | 40397 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 53 |  | 4 | 1 | DECIMAL | Periodic | No | Setpoint |  |  | sec.
HI REF LVL | 03 | 40409 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Low Oil Level | 03 | 40439 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
LO LIQ TMP | 03 | 40455 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO LIQ UNLD | 03 | 40456 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
MDP OIL DIFF | 03 | 40505 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
No OIL Flow | 03 | 40511 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
OIL Flow Diff | 03 | 40521 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG