## LCWT1-0515F
Controller Type | Device Type | Chiller Code
TC2 OLD HGB-SI-WO-ECO TOR1 | CHILLER | 1
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Compressor 1 Supply Relay | 01 | 00002 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
LLS 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Suction Pressure 1 | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Discharge Pressure 1 | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | PSIG
Cooler Water Out Temp | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 40 | 80 | F
Cooler Water In Temp | 04 | 30004 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 44 | 80 | F
Suction Temperature 1 | 04 | 30005 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Discharge Temperature 1 | 04 | 30006 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 50 | 160 | F
Condenser Water In Temp | 04 | 30007 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 65 | 95 | F
Condenser Water Out Temp | 04 | 30008 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 70 | 95 | F
REF LVL1 | 04 | 30009 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 0 | 99 | %
Liquid Temp 1 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Cooler Flow Switch | 04 | 30013 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Condenser Flow Switch | 04 | 30014 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | Status | Yes
SPPR 1 | 04 | 30016 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | Status | Yes
Comp Fault 1 | 04 | 30017 | 01 | 9600 | Digital-Inputs | 5 |  | 4 | 1 | DECIMAL | Status | Yes
IGV % | 04 | 30019 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Suction Pressure 1 | 04 | 30020 | 01 | 9600 | Analog-Inputs | 12 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 28 | 60 | PSIG
Discharge Pressure 1 | 04 | 30021 | 01 | 9600 | Analog-Inputs | 13 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 40 | 145 | PSIG
Cavity Temp 1 | 04 | 30022 | 01 | 9600 | Analog-Inputs | 14 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 70 | 150 | F
Inverter Temp 1 | 04 | 30023 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 70 | 150 | F
Power KW1 | 04 | 30024 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | KW
Surge Speed | 04 | 30025 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 10 | DECIMAL | Periodic | Yes |  |  |  | rpm
Actual RPM | 04 | 30026 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 10 | DECIMAL | Periodic | Yes |  |  |  | rpm
DCVoltage1 | 04 | 30027 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 500 | 690 | V
Compressor 1 Current | 04 | 30028 | 01 | 9600 | Analog-Inputs | 20 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Main Voltage | 04 | 30029 | 01 | 9600 | Analog-Inputs | 21 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 380 | 460 | V
Motor Alarm | 04 | 30030 | 01 | 9600 | Digital-Inputs | 6 |  | 4 | 1 | DECIMAL | Status | Yes
Bearing Alarm | 04 | 30031 | 01 | 9600 | Digital-Inputs | 7 |  | 4 | 1 | DECIMAL | Status | Yes
Min PSI RT | 04 | 30032 | 01 | 9600 | Analog-Inputs | 22 |  | 4 | 0.1 | DECIMAL | Periodic | Yes
BMS RUN | 04 | 30033 | 01 | 9600 | Digital-Inputs | 8 |  | 4 | 1 | DECIMAL | Status | Yes
EVA APPRO 1 | 04 | 30034 | 01 | 9600 | Analog-Inputs | 23 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 0 | 5 | F
Condenser Approach | 04 | 30035 | 01 | 9600 | Analog-Inputs | 24 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 0 | 5 | F
HGB Off | 04 | 30036 | 01 | 9600 | Analog-Inputs | 25 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
HGB On | 04 | 30037 | 01 | 9600 | Analog-Inputs | 26 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Suction Superheat 1 | 04 | 30038 | 01 | 9600 | Analog-Inputs | 27 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Discharge Superheat 1 | 04 | 30039 | 01 | 9600 | Analog-Inputs | 28 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 7 | 22 | F
Volt RMK | 04 | 30040 | 01 | 9600 | Digital-Inputs | 9 |  | 4 | 1 | DECIMAL | Status | Yes
Flow Switch 1 | 04 | 30041 | 01 | 9600 | Digital-Inputs | 10 |  | 4 | 1 | DECIMAL | Status | Yes
SRG Offset | 04 | 30042 | 01 | 9600 | Analog-Inputs | 29 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | rpm
Comp Surge | 04 | 30043 | 01 | 9600 | Digital-Inputs | 11 |  | 4 | 1 | DECIMAL | Status | Yes
Min IGV | 04 | 30044 | 01 | 9600 | Digital-Inputs | 12 |  | 4 | 1 | DECIMAL | Status | Yes
IGV/SRG | 04 | 30045 | 01 | 9600 | Digital-Inputs | 13 |  | 4 | 1 | DECIMAL | Status | Yes
Electronic Expansion Valve 1 | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
HGB 1 | 04 | 30202 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
CND VALV | 04 | 30204 | 01 | 9600 | Analog-Outputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Demand | 04 | 30205 | 01 | 9600 | Control-Information | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Start RPM | 04 | 30206 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | rpm
Loading | 04 | 30207 | 01 | 9600 | Control-Information | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Chiller State | 04 | 30306 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Status | No
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Status | No
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps Delay | 04 | 30317 | 01 | 9600 | Control-Information | 8 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 9 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp 1 FLA | 04 | 30319 | 01 | 9600 | Control-Information | 10 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp 1 | 04 | 30327 | 01 | 9600 | Analog-Inputs | 30 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Suction Superheat 1 | 04 | 30328 | 01 | 9600 | Analog-Inputs | 31 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Saturated Discharge Temp 1 | 04 | 30329 | 01 | 9600 | Analog-Inputs | 32 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | F
Discharge Superheat 1 | 04 | 30330 | 01 | 9600 | Analog-Inputs | 33 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 7 | 22 | F
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | Status | No
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | Status | No
RH Compressor 1 On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | hrs
RH Compressor 1 Supply | 04 | 30679 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | hrs
RH LLS1 | 04 | 30680 | 01 | 9600 | Runhours | 3 |  | 4 | 1 | DECIMAL | Periodic | No |  |  |  | hrs
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
REF LVL TARG | 03 | 40309 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
REF LVL ZONE | 03 | 40310 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV Load DIV | 03 | 40314 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV MAX | 03 | 40316 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | Sec
MAX Demand % | 03 | 40330 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MIN VFD % | 03 | 40331 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
MAX ADJUST | 03 | 40332 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST | 03 | 40333 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
SLIDE SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
A-CYC OFF-ON | 03 | 40359 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
PMP DWN OFF | 03 | 40361 | 01 | 9600 | Setpoints | 36 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
PMP DWN DLAY | 03 | 40362 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
A-CYC ON-ON | 03 | 40363 | 01 | 9600 | Setpoints | 38 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | min
HI AMPS | 03 | 40375 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO Disc SPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 50 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 52 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI Inverter Temp | 03 | 40394 | 01 | 9600 | Setpoints | 53 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
High Cavity Temp | 03 | 40395 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
ERCON ON | 03 | 40399 | 01 | 9600 | Setpoints | 55 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
HI REF LVL | 03 | 40409 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LO REF LVL | 03 | 40410 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
unloaded off | 03 | 40451 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO LIQ TMP | 03 | 40455 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LO LIQ UNLD | 03 | 40456 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
SPPR Fault | 03 | 40466 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
Surge RPM Diff | 03 | 40481 | 01 | 9600 | Setpoints | 65 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | rpm
Stage 1 | 03 | 40482 | 01 | 9600 | Setpoints | 66 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
temp diff | 03 | 40491 | 01 | 9600 | Setpoints | 67 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 68 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
Surge Trip | 03 | 40511 | 01 | 9600 | Setpoints | 69 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | rpm
Turbocor Comp fault | 03 | 40512 | 01 | 9600 | Setpoints | 70 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint

## Status
Register Address | State |  |  | Description
30013 | 0 |  |  | NO FLOW
30013 | 1 |  |  | FLOW
30014 | 0 |  |  | NO FLOW
30014 | 1 |  |  | FLOW
30015 | 0 |  |  | ON
30015 | 1 |  |  | OFF
30016 | 0 |  |  | NORMAL
30016 | 1 |  |  | ALARM
30017 | 0 |  |  | OK
30017 | 1 |  |  | FAULT
30030 | 0 |  |  | OFF
30030 | 1 |  |  | ON
30031 | 0 |  |  | OFF
30031 | 1 |  |  | ON
30033 | 0 |  |  | STOP
30033 | 1 |  |  | RUN
30040 | 0 |  |  | OK
30040 | 1 |  |  | FAULT
30041 | 0 |  |  | NO FLOW
30041 | 1 |  |  | FLOW
30043 | 0 |  |  | FAULT
30043 | 1 |  |  | OK
30044 | 0 |  |  | OK
30044 | 1 |  |  | Fault
30045 | 0 |  |  | OK
30045 | 1 |  |  | Fault
30306 | 0 |  |  | UNIT IN POWER UP
30306 | 1 |  |  | POWER LOSS DELAY
30306 | 2 |  |  | NO RUN- I/O LOST
30306 | 3 |  |  | UNIT IN LOCKOUT
30306 | 4 |  |  | UNIT IS OFF
30306 | 5 |  |  | UNIT IS HOLDING
30306 | 6 |  |  | UNIT UNLOADING
30306 | 7 |  |  | UNIT IS LOADING
30306 | 8 |  |  | OFF-SMOKE ALARM
30306 | 9 |  |  | RUN/STOP SW OFF
30306 | 10 |  |  | SCHEDULED OFF
30306 | 11 |  |  | OFF-NO FLOW(s)
30306 | 12 |  |  | OFF-WTR PSI FLOW
30306 | 13 |  |  | AMBIENT OFF
30306 | 14 |  |  | PROCESS HEAT OFF
30306 | 15 |  |  | UNIT IS UNLOADED
30306 | 16 |  |  | UNIT IS LOADED
30306 | 17 |  |  | OFF TMP-ICE MADE
30306 | 18 |  |  | ECONOMIZER ONLY
30306 | 19 |  |  | SWITCHING MODES
30306 | 20 |  |  | UNIT SMOKE UNLDG
30306 | 21 |  |  | UNIT OFF UNLDING
30306 | 22 |  |  | UNIT DMD UNLDING
30306 | 23 |  |  | UNIT HEAT UNLDNG
30306 | 24 |  |  | UNLDING RUN CMPS
30306 | 25 |  |  | OPENING BYP VLV
30306 | 26 |  |  | CMP RAMPING UP
30306 | 27 |  |  | CLOSING BYP VLV
30306 | 28 |  |  | FACTORY STARTUP
30306 | 29 |  |  | MAXIMUM RUN TIME
30306 | 30 |  |  | NOT USED
30306 | 31 |  |  | OFF-FIRE ALARM
30306 | 32 |  |  | UNIT HEAT HOLDG
30306 | 33 |  |  | CMP SPD OPTIMIZE
30306 | 34 |  |  | UNUSED STATE
30306 | 35 |  |  | RS-STARTING COMP
30306 | 36 |  |  | RS-LOADING
30306 | 37 |  |  | RS-HOLDING
30306 | 38 |  |  | UNIT IS OFF/TEMP
30307 | 0 |  |  | LOST IO LOCKED
30307 | 1 |  |  | CMP LOCKED OUT
30307 | 2 |  |  | SWITCHED OFF
30307 | 3 |  |  | UNLD & PMPDWN
30307 | 4 |  |  | CMP ANTICYCLE
30307 | 5 |  |  | CMP OFF/READY
30307 | 6 |  |  | OIL PMP LUBING
30307 | 7 |  |  | CMP IN STARTUP
30307 | 8 |  |  | CMP UNLOADED
30307 | 9 |  |  | CMP UNLD STEP1
30307 | 10 |  |  | CMP UNLD STEP2
30307 | 11 |  |  | CMP IS HOLDING
30307 | 12 |  |  | CMP IS LOADING
30307 | 13 |  |  | CMP IS UNLDING
30307 | 14 |  |  | CMP IS RUNNING
30307 | 15 |  |  | FAST UNLOADING
30307 | 16 |  |  | LO SUCT UNLOAD
30307 | 17 |  |  | LO SUCT HOLD
30307 | 18 |  |  | HI DISC UNLOAD
30307 | 19 |  |  | HI DISC HOLD
30307 | 20 |  |  | SAFETY TRIPPED
30307 | 21 |  |  | LO TEMP UNLOAD
30307 | 22 |  |  | LO TEMP HOLD
30307 | 23 |  |  | HI AMP HOLD
30307 | 24 |  |  | HI DIS TMP HLD
30307 | 25 |  |  | CMP IS AT 40%
30307 | 26 |  |  | CMP IS AT 70%
30307 | 27 |  |  | HI WATER HOLD
30307 | 28 |  |  | EXTRA 70% STEP
30307 | 29 |  |  | OFF-LO OIL TMP
30307 | 30 |  |  | HI AMP UNLDING
30307 | 31 |  |  | DEF PREPMP OUT
30307 | 32 |  |  | DEFROSTING
30307 | 33 |  |  | DEF PUMP DOWN
30307 | 34 |  |  | HI TEMP UNLOAD
30307 | 35 |  |  | HI TEMP HOLD
30307 | 36 |  |  | SCROLL STEP 1
30307 | 37 |  |  | SCROLL STEP 2
30307 | 38 |  |  | SCROLL STEP 3
30307 | 39 |  |  | SCROLL STEP 4
30307 | 40 |  |  | ON OIL RECOVRY
30307 | 41 |  |  | WAIT P-RATIO
30307 | 42 |  |  | CMP GROUP OFF
30307 | 43 |  |  | CLOSING VANES
30307 | 44 |  |  | TimingVaneOpn
30307 | 45 |  |  | TimingVaneCls
Register Address Type | Status/ Alarm Type | Register Address Point | Alarm Point | Description
30668 | 0 | 30673 | Not Used (255) | POWER FAILED
30668 | 1 | 30673 | Not Used (255) | COMPUTER RESET
30668 | 2 | 30673 | Not Used (255) | BATTERY FAILED
30668 | 3 | 30673 | Not Used (255) | INVERTER TEMP
30668 | 4 | 30673 | Not Used (255) | DISCHARGE TEMP
30668 | 5 | 30673 | Not Used (255) | SUCTION PSI
30668 | 6 | 30673 | Not Used (255) | DISCHARGE PSI
30668 | 7 | 30673 | Not Used (255) | 3PHASE OVER AMPS
30668 | 8 | 30673 | Not Used (255) | ALARMS CLEARED
30668 | 9 | 30673 | Not Used (255) | POWER RETURNED
30668 | 10 | 30673 | Not Used (255) | CAVITY TEMP
30668 | 11 | 30673 | Not Used (255) | STPT CHANGED
30668 | 12 | 30673 | Not Used (255) | RO TO MANON + Point #
30668 | 13 | 30673 | Not Used (255) | AO TO MANUAL + Point #
30668 | 14 | 30673 | Not Used (255) | SI TO MANUAL + Point #
30668 | 15 | 30673 | Not Used (255) | POINT INFO CLEAR
30668 | 16 | 30673 | Not Used (255) | CLOCK SET
30668 | 17 | 30673 | Not Used (255) | CFG DOWNLOADED
30668 | 18 | 30673 | Not Used (255) | ROTATED LEAD\0
30668 | 19 | 30673 | Not Used (255) | SI OFFSET
30668 | 20 | 30673 | Not Used (255) | SI TYPE
30668 | 21 | 30673 | Not Used (255) | LEAV FLUID TEMP
30668 | 22 | 30673 | Not Used (255) | PRESSURE RATIO
30668 | 23 | 30673 | Not Used (255) | BEAR MOTOR CMP
30668 | 24 | 30673 | Not Used (255) | CMP SENSOR FLT
30668 | 25 | 30673 | Not Used (255) | DAYLIGHT SAVINGS
30668 | 26 | 30673 | Not Used (255) | LOCKOUT RESET
30668 | 27 | 30673 | Not Used (255) | FIRMWARE LOADED
30668 | 28 | 30673 | Not Used (255) | BOOTLOADER ERROR
30668 | 29 | 30673 | Not Used (255) | RS485 CHANGED
30668 | 30 | 30673 | Not Used (255) | ETHERNET CHANGED
30668 | 31 | 30673 | Not Used (255) | INVALID CFG CSUM
30668 | 32 | 30673 | Not Used (255) | INVALID CFG VER
30668 | 33 | 30673 | Not Used (255) | LOST RO COMM
30668 | 34 | 30673 | Not Used (255) | LOST SI COMM
30668 | 35 | 30673 | Not Used (255) | BACnet Port Chg
30668 | 36 | 30673 | Not Used (255) | WATCHDOG RESET
30668 | 37 | 30673 | Not Used (255) | SRC TEMP FAULT
30668 | 38 | 30673 | Not Used (255) | EMERGENCY STOP
30668 | 39 | 30673 | Not Used (255) | OFF-SMOKE ALARM
30668 | 40 | 30673 | Not Used (255) | RO TO AUTO + Point #
30668 | 41 | 30673 | Not Used (255) | AO TO AUTO + Point #
30668 | 42 | 30673 | Not Used (255) | SI TO AUTO + Point #
30668 | 43 | 30673 | Not Used (255) | PHASE LOSS
30668 | 44 | 30673 | Not Used (255) | RO TO MANOFF + Point #
30668 | 45 | 30673 | Not Used (255) | TURBO LOCK OUT
30668 | 46 | 30673 | Not Used (255) | TURBO WIND TMP
30668 | 47 | 30673 | Not Used (255) | TURBOCOR SSH FLT
30668 | 48 | 30673 | Not Used (255) | TURB RESERVED
30668 | 49 | 30673 | Not Used (255) | CND/CTG FAULT
30668 | 50 | 30673 | Not Used (255) | LOST IO SHUTDOWN
30668 | 51 | 30673 | Not Used (255) | SMOKE PURGE
30668 | 52 | 30673 | Not Used (255) | INVALID CFG TYPE
30668 | 53 | 30673 | Not Used (255) | ENGY WHEEL ALARM
30668 | 54 | 30673 | Not Used (255) | LOST I/O RESTART
30668 | 55 | 30673 | Not Used (255) | OFF-FIRE ALARM
30668 | 56 | 30673 | Not Used (255) | NO IGNITION
30668 | 57 | 30673 | Not Used (255) | PURGE RESTART
30668 | 58 | 30673 | Not Used (255) | TMP OFF-ICE MADE
30668 | 59 | 30673 | Not Used (255) | LVL OFF-ICE MADE
30668 | 60 | 30673 | Not Used (255) | START MAKING ICE
30668 | 61 | 30673 | Not Used (255) | INTERNAL RAM
30668 | 62 | 30673 | Not Used (255) | EXTERNAL RAM 0
30668 | 63 | 30673 | Not Used (255) | EXTERNAL RAM 1
30668 | 64 | 30673 | Not Used (255) | LOST A/D CONVTR
30668 | 65 | 30673 | Not Used (255) | LOST DISPLAY
30668 | 66 | 30673 | Not Used (255) | LOST IO COMP
30668 | 67 | 30673 | Not Used (255) | LOST KEYPAD
30668 | 68 | 30673 | Not Used (255) | CFG FLASH PTR
30668 | 69 | 30673 | Not Used (255) | NETWORK ADDR CHG
30668 | 70 | 30673 | Not Used (255) | UPDATED FLASHCFG
30668 | 71 | 30673 | Not Used (255) | LOST A/D SHUTDWN
30668 | 72 | 30673 | Not Used (255) | CF CARD REMOVED
30668 | 73 | 30673 | Not Used (255) | CF CARD INSERTED
30668 | 74 | 30673 | Not Used (255) | CF INIT ERROR
30668 | 75 | 30673 | Not Used (255) | MCS-STAT OFFLINE
30668 | 76 | 30673 | Not Used (255) | BACnet Addr Chg
30668 | 77 | 30673 | Not Used (255) | FORCE MCS PROCOL
30668 | 78 | 30673 | Not Used (255) | UNUSED ALARM #78
30668 | 79 | 30673 | Not Used (255) | UNUSED ALARM #79
30668 | 80 | 30673 | 1 | CW OUT TRGT
30668 | 81 | 30673 | 1 | CTRL ZONE+
30668 | 82 | 30673 | 1 | CTRL ZONE-
30668 | 88 | 30673 | 1 | REF LVL TARG
30668 | 89 | 30673 | 1 | REF LVL ZONE
30668 | 90 | 30673 | 1 | EXV LOAD ADJ
30668 | 91 | 30673 | 1 | EXV FINE ADJ
30668 | 92 | 30673 | 1 | EXV COURSE
30668 | 93 | 30673 | 1 | EXV Load DIV
30668 | 94 | 30673 | 1 | EXV MIN%
30668 | 95 | 30673 | 1 | EXV MAX%
30668 | 97 | 30673 | 1 | LOSUCTPSIDLY
30668 | 98 | 30673 | 1 | EXV DELAY
30668 | 99 | 30673 | 1 | EXV STRT TME
30668 | 102 | 30673 | 1 | POWERUP DLAY
30668 | 104 | 30673 | 1 | STEP SENSIT
30668 | 105 | 30673 | 1 | STEP DELAY
30668 | 106 | 30673 | 1 | MAX ROC-
30668 | 107 | 30673 | 1 | MAX ROC+
30668 | 108 | 30673 | 1 | ROC INTERVAL
30668 | 109 | 30673 | 1 | MAX DEMAND%
30668 | 110 | 30673 | 1 | MIN VFD %
30668 | 111 | 30673 | 1 | MAX ADJUST %
30668 | 112 | 30673 | 1 | MIN ADJUST %
30668 | 113 | 30673 | 1 | SLIDE SENSIT
30668 | 127 | 30673 | 1 | CND DELAY
30668 | 128 | 30673 | 1 | CNDVLVstart%
30668 | 129 | 30673 | 1 | CND VLV TARG
30668 | 130 | 30673 | 1 | CND VLV DIV
30668 | 131 | 30673 | 1 | CND VLV MIN
30668 | 132 | 30673 | 1 | CND VLV ROC-
30668 | 133 | 30673 | 1 | CND VLV MULT
30668 | 134 | 30673 | 1 | CND VLV ADJ
30668 | 135 | 30673 | 1 | PULSE DELAY
30668 | 138 | 30673 | 1 | A-CYC OFF-ON
30668 | 140 | 30673 | 1 | PMP DWN OFF
30668 | 141 | 30673 | 1 | PMP DWN DLAY
30668 | 142 | 30673 | 1 | A-CYC ON-ON
30668 | 143 | 30673 | 1 | COMP MIN RUN
30668 | 154 | 30673 | 1 | HI AMPS %
30668 | 155 | 30673 | 1 | LOampNoSTART
30668 | 156 | 30673 | 1 | LOW SUCTION
30668 | 157 | 30673 | 1 | LO SUCT UNLD
30668 | 158 | 30673 | 1 | LO SUCT RELD
30668 | 159 | 30673 | 1 | LOgas/LLsFLT
30668 | 160 | 30673 | 1 | HI DISC PSI
30668 | 161 | 30673 | 1 | HI DISC UNLD
30668 | 162 | 30673 | 1 | HI DISC RELD
30668 | 163 | 30673 | 1 | LO DiscSPRHT
30668 | 166 | 30673 | 1 | HI DISCH TMP
30668 | 167 | 30673 | 1 | DIS TMP UNLD
30668 | 168 | 30673 | 1 | DIS TMP RELD
30668 | 173 | 30673 | 1 | HI Inv TMP
30668 | 174 | 30673 | 1 | Hi Cav Tmp
30668 | 178 | 30673 | 1 | ERCON ON%
30668 | 180 | 30673 | 1 | SafetyHold
30668 | 188 | 30673 | 1 | HI REF LVL
30668 | 189 | 30673 | 1 | LO REF LVL
30668 | 190 | 30673 | 1 | FREEZE
30668 | 230 | 30673 | 1 | Unloaded Off
30668 | 234 | 30673 | 1 | LO LQD TMP
30668 | 235 | 30673 | 1 | LO LQD UNLD
30668 | 245 | 30673 | 1 | Sppr Fault
30668 | 250 | 30673 | 1 | FLA COMP#1
30668 | 260 | 30673 | 1 | SurgeRpmDiff
30668 | 261 | 30673 | 1 | Stage 1%
30668 | 270 | 30673 | 1 | Temp Diff
30668 | 281 | 30673 | 1 | HI EVP DEL T
30668 | 290 | 30673 | 1 | Srg/IGV Trip
30668 | 291 | 30673 | 1 | Turb Cmp Flt
30668 | 310 | 30673 | 0 | Alarm COM SUCT P
30668 | 310 | 30673 | 1 | Alarm COM DIS P
30668 | 310 | 30673 | 2 | Alarm WaterOUT
30668 | 310 | 30673 | 3 | Alarm Water IN
30668 | 310 | 30673 | 4 | Alarm SucTmp1
30668 | 310 | 30673 | 5 | Alarm DiscTmp1
30668 | 310 | 30673 | 6 | Alarm Cond In
30668 | 310 | 30673 | 7 | Alarm Cond Out
30668 | 310 | 30673 | 8 | Alarm REFLVL1
30668 | 310 | 30673 | 9 | Alarm Liqd temp
30668 | 310 | 30673 | 10 | Alarm SPARE M-11
30668 | 310 | 30673 | 11 | Alarm SPARE M-12
30668 | 310 | 30673 | 12 | Alarm CLR FLOW
30668 | 310 | 30673 | 13 | Alarm CND FLOW
30668 | 310 | 30673 | 14 | Alarm SYS1 OFF
30668 | 310 | 30673 | 15 | Alarm SPPR1
30668 | 310 | 30673 | 16 | Alarm CMP FAULT1
30668 | 310 | 30673 | 17 | Alarm CTRL MODE
30668 | 310 | 30673 | 18 | Alarm IGV%
30668 | 310 | 30673 | 19 | Alarm SP1
30668 | 310 | 30673 | 20 | Alarm DP1
30668 | 310 | 30673 | 21 | Alarm CAV TMP1
30668 | 310 | 30673 | 22 | Alarm INV TMP1
30668 | 310 | 30673 | 23 | Alarm POWER
30668 | 310 | 30673 | 24 | Alarm SURGE SPD
30668 | 310 | 30673 | 25 | Alarm ACTUAL RPM
30668 | 310 | 30673 | 26 | Alarm DC_VOLT
30668 | 310 | 30673 | 27 | Alarm CURRENT 1
30668 | 310 | 30673 | 28 | Alarm MainVoltge
30668 | 310 | 30673 | 29 | Alarm MOTOR_ALRM
30668 | 310 | 30673 | 30 | Alarm BeargAlarm
30668 | 310 | 30673 | 31 | Alarm MIN_PSI_RT
30668 | 310 | 30673 | 32 | Alarm BMS RUN
30668 | 310 | 30673 | 33 | Alarm EVAP APPR
30668 | 310 | 30673 | 34 | Alarm COND APPR
30668 | 310 | 30673 | 35 | Alarm HGB OFF
30668 | 310 | 30673 | 36 | Alarm HGB ON
30668 | 310 | 30673 | 37 | Alarm SSH
30668 | 310 | 30673 | 38 | Alarm DSH
30668 | 310 | 30673 | 39 | Alarm VOLT RMK
30668 | 310 | 30673 | 40 | Alarm CLRCND FLW
30668 | 310 | 30673 | 41 | Alarm SRG OFFSET
30668 | 310 | 30673 | 42 | Alarm CMPOTOFSRG
30668 | 310 | 30673 | 43 | Alarm MIN IGV
30668 | 310 | 30673 | 44 | Alarm IGV/SRG
30668 | 311 | 30673 | 0 | Alarm CMP1 ON
30668 | 311 | 30673 | 1 | Alarm CMP1 SPPLY
30668 | 311 | 30673 | 2 | Alarm LLS1
30668 | 311 | 30673 | 3 | Alarm SPAREM-4
30668 | 311 | 30673 | 4 | Alarm SPAREM-5
30668 | 311 | 30673 | 5 | Alarm SPAREM-6
30668 | 311 | 30673 | 6 | Alarm SPAREM-7
30668 | 311 | 30673 | 7 | Alarm SPAREM-8
30668 | 311 | 30673 | 8 | Alarm LstMdbsCom
30668 | 311 | 30673 | 9 | Alarm ALARM
30668 | 311 | 30673 | 10 | Alarm Vr1
30668 | 311 | 30673 | 11 | Alarm Vr2
30668 | 311 | 30673 | 12 | Alarm Vr3
30668 | 311 | 30673 | 13 | Alarm Vr4
30668 | 338 | 30673 | Not Used (255) | BRAKE CHECK
30668 | 339 | 30673 | Not Used (255) | POWER CARD TEMP
30668 | 340 | 30673 | Not Used (255) | EARTH FAULT
30668 | 341 | 30673 | Not Used (255) | CTRL CARD TEMP
30668 | 342 | 30673 | Not Used (255) | CTRL WORD TO
30668 | 343 | 30673 | Not Used (255) | OVER CURRENT
30668 | 344 | 30673 | Not Used (255) | TORQUE LIMIT
30668 | 345 | 30673 | Not Used (255) | MOTOR TH OVER
30668 | 346 | 30673 | Not Used (255) | MOTOR ETR OVER
30668 | 347 | 30673 | Not Used (255) | INVERTER OVERLD
30668 | 348 | 30673 | Not Used (255) | DC UNDER VOLT
30668 | 349 | 30673 | Not Used (255) | DC OVER VOLT
30668 | 350 | 30673 | Not Used (255) | SHORT CIRCUIT
30668 | 351 | 30673 | Not Used (255) | INRUSH FAULT
30668 | 352 | 30673 | Not Used (255) | MAIN PHASE LOSS
30668 | 353 | 30673 | Not Used (255) | AMA NOT OK
30668 | 354 | 30673 | Not Used (255) | LIVE ZERO ERROR
30668 | 355 | 30673 | Not Used (255) | INTERNAL FAULT
30668 | 356 | 30673 | Not Used (255) | BRAKE OVERLOAD
30668 | 357 | 30673 | Not Used (255) | U PHASE LOSS
30668 | 358 | 30673 | Not Used (255) | V PHASE LOSS
30668 | 359 | 30673 | Not Used (255) | W PHASE LOSS
30668 | 360 | 30673 | Not Used (255) | FIELDBUS FAULT
30668 | 361 | 30673 | Not Used (255) | 24V SUPPLY LOW
30668 | 362 | 30673 | Not Used (255) | MAINS FAILURE
30668 | 363 | 30673 | Not Used (255) | 1.8V SUPPLY LOW
30668 | 364 | 30673 | Not Used (255) | BRAKE RESISTOR
30668 | 365 | 30673 | Not Used (255) | BRAKE IGBT
30668 | 366 | 30673 | Not Used (255) | OPTION CHANGE
30668 | 367 | 30673 | Not Used (255) | DRIVE INIT
30668 | 368 | 30673 | Not Used (255) | SAFE STOP
30668 | 369 | 30673 | Not Used (255) | MECH BRAKE LOW
30668 | 370 | 30673 | Not Used (255) | SERIAL TIMEOUT
30668 | 371 | 30673 | Not Used (255) | MAINS FAILURE
30668 | 372 | 30673 | Not Used (255) | ENVELOPE FAULT
30668 | 373 | 30673 | Not Used (255) | ENVELOP INIT FLT
30668 | 374 | 30673 | Not Used (255) | COMP SHORT CYCLE
30668 | 375 | 30673 | Not Used (255) | HIGH OIL TEMP
30668 | 376 | 30673 | Not Used (255) | LOW OIL LEVEL
30668 | 377 | 30673 | Not Used (255) | UNUSED
30668 | 378 | 30673 | Not Used (255) | MOTOR OVERLOAD
30668 | 379 | 30673 | Not Used (255) | WRONG PHASE SEQ
30668 | 380 | 30673 | Not Used (255) | MTR THERML OVRLD
30668 | 381 | 30673 | Not Used (255) | INVERTER FAULT
30668 | 382 | 30673 | Not Used (255) | OVER CURRENT
30668 | 383 | 30673 | Not Used (255) | OVER VOLTAGE
30668 | 384 | 30673 | Not Used (255) | UNDER VOLTAGE
30668 | 385 | 30673 | Not Used (255) | FC OVER TEMP
30668 | 386 | 30673 | Not Used (255) | HW CONFIG FAULT
30668 | 387 | 30673 | Not Used (255) | PWR DATA CFG FLT
30668 | 388 | 30673 | Not Used (255) | MTR DATA CFG FLT
30668 | 389 | 30673 | Not Used (255) | HARDWARE FAULT
30668 | 390 | 30673 | Not Used (255) | UNUSED
30668 | 391 | 30673 | Not Used (255) | TEMP SENSOR FLT
30668 | 392 | 30673 | Not Used (255) | UNUSED
30668 | 393 | 30673 | Not Used (255) | UNUSED
30668 | 394 | 30673 | Not Used (255) | UNUSED
30668 | 395 | 30673 | Not Used (255) | UNUSED
30668 | 396 | 30673 | Not Used (255) | UNUSED
30668 | 397 | 30673 | Not Used (255) | UNUSED
30668 | 398 | 30673 | Not Used (255) | UNUSED
30668 | 399 | 30673 | Not Used (255) | UNUSED
30668 | 400 | 30673 | Not Used (255) | UNUSED
30668 | 401 | 30673 | Not Used (255) | UNUSED
30668 | 402 | 30673 | Not Used (255) | CHILLER OFFLINE
30668 | 403 | 30673 | Not Used (255) | UPDATED RAM CFG
30668 | 404 | 30673 | Not Used (255) | LUBE-VANES FAULT
30668 | 405 | 30673 | Not Used (255) | VANES NOT MOVING
30668 | 406 | 30673 | Not Used (255) | CMP NOT OFF-AMPS
30668 | 407 | 30673 | Not Used (255) | DMPR MIX AIR FLT
30668 | 408 | 30673 | Not Used (255) | DMPR FEEDBCK FLT
30668 | 409 | 30673 | Not Used (255) | DMP POS OUTRANGE
30668 | 410 | 30673 | Not Used (255) | DMPR NOT AT MAX
30668 | 411 | 30673 | Not Used (255) | DMPR NOT AT MIN
30668 | 412 | 30673 | Not Used (255) | DMPR NOT OPENING
30668 | 413 | 30673 | Not Used (255) | DMPR NOT CLOSING
30668 | 414 | 30673 | Not Used (255) | DMPR STUCK OPEN
30668 | 415 | 30673 | Not Used (255) | DMPR STUCK CLOSD
30668 | 416 | 30673 | Not Used (255) | DMPR RET=AMB TMP
30668 | 417 | 30673 | Not Used (255) | RO TO CMP FIXED%
30668 | 418 | 30673 | Not Used (255) | CMP FIXED%notCMP
30668 | 419 | 30673 | Not Used (255) | HW/SW/Hall Flt
30668 | 420 | 30673 | Not Used (255) | SWPeak/Hw/AC RMS
30668 | 421 | 30673 | Not Used (255) | DC OVER VOLTAGE
30668 | 422 | 30673 | Not Used (255) | DC UNDER VOLTAGE
30668 | 423 | 30673 | Not Used (255) | AC OVER VOLTAGE
30668 | 424 | 30673 | Not Used (255) | AC UNDER VOLTAGE
30668 | 425 | 30673 | Not Used (255) | UNUSED
30668 | 426 | 30673 | Not Used (255) | UNUSED
30668 | 427 | 30673 | Not Used (255) | Hi PSI Switch
30668 | 428 | 30673 | Not Used (255) | UNUSED
30668 | 429 | 30673 | Not Used (255) | UNUSED
30668 | 430 | 30673 | Not Used (255) | Invrtr OVER TEMP
30668 | 431 | 30673 | Not Used (255) | PFC IGBTOverTemp
30668 | 432 | 30673 | Not Used (255) | LOST ROTOR
30668 | 433 | 30673 | Not Used (255) | UNUSED
30668 | 434 | 30673 | Not Used (255) | UNUSED
30668 | 435 | 30673 | Not Used (255) | LOW DC VOLTAGE
30668 | 436 | 30673 | Not Used (255) | UNUSED
30668 | 437 | 30673 | Not Used (255) | EnvTorqueLmtTime
30668 | 438 | 30673 | Not Used (255) | PIMFoldBack Time
30668 | 439 | 30673 | Not Used (255) | Cur.FoldBackTime
30668 | 440 | 30673 | Not Used (255) | UNUSED
30668 | 441 | 30673 | Not Used (255) | UNUSED
30668 | 442 | 30673 | Not Used (255) | NoCommDataFor30s
30668 | 443 | 30673 | Not Used (255) | SI2FltLoTemp/Srt
30668 | 444 | 30673 | Not Used (255) | UNUSED
30668 | 445 | 30673 | Not Used (255) | UNUSED
30668 | 446 | 30673 | Not Used (255) | HI INVERTER TEMP
30668 | 447 | 30673 | Not Used (255) | HIGH PFC TEMP
30668 | 448 | 30673 | Not Used (255) | No DSP/PFC Comms
30668 | 449 | 30673 | Not Used (255) | Comm to DSP Lost
30668 | 450 | 30673 | Not Used (255) | UNUSED
30668 | 451 | 30673 | Not Used (255) | InvrtrAmpsImblnc
30668 | 452 | 30673 | Not Used (255) | UNUSED
30668 | 453 | 30673 | Not Used (255) | Drive EEPROM Flt
30668 | 454 | 30673 | Not Used (255) | UNUSED
30668 | 455 | 30673 | Not Used (255) | UNUSED
30668 | 456 | 30673 | Not Used (255) | SI1Flt-HiPSI Low
30668 | 457 | 30673 | Not Used (255) | CompConfigError
30668 | 458 | 30673 | Not Used (255) | HiPsiType Error
30668 | 459 | 30673 | Not Used (255) | UNUSED
30668 | 460 | 30673 | Not Used (255) | UNUSED
30668 | 461 | 30673 | Not Used (255) | UNUSED
30668 | 462 | 30673 | Not Used (255) | UNUSED
30668 | 463 | 30673 | Not Used (255) | UNUSED
30668 | 464 | 30673 | Not Used (255) | UNUSED
30668 | 465 | 30673 | Not Used (255) | UNUSED
30668 | 466 | 30673 | Not Used (255) | UNUSED
30668 | 467 | 30673 | Not Used (255) | UNUSED
30668 | 468 | 30673 | Not Used (255) | UNUSED
30668 | 469 | 30673 | Not Used (255) | SI2Flt-LoTmpOpen
30668 | 470 | 30673 | Not Used (255) | UNUSED
30668 | 471 | 30673 | Not Used (255) | UNUSED
30668 | 472 | 30673 | Not Used (255) | InvrtrTmpSI Open
30668 | 473 | 30673 | Not Used (255) | PFC Temp SI Open
30668 | 474 | 30673 | Not Used (255) | UNUSED
30668 | 475 | 30673 | Not Used (255) | UNUSED
30668 | 476 | 30673 | Not Used (255) | UNUSED
30668 | 477 | 30673 | Not Used (255) | UNUSED
30668 | 478 | 30673 | Not Used (255) | UNUSED
30668 | 479 | 30673 | Not Used (255) | UNUSED
30668 | 480 | 30673 | Not Used (255) | UNUSED
30668 | 481 | 30673 | Not Used (255) | UNUSED
30668 | 482 | 30673 | Not Used (255) | FltLimit Lockout
30668 | 483 | 30673 | Not Used (255) | VANE CLS/OPN FLT
30668 | 484 | 30673 | Not Used (255) | VANE NOT CLOSING
30668 | 485 | 30673 | Not Used (255) | VANE NOT OPENING
30668 | 486 | 30673 | Not Used (255) | VANES CALIBRATED
30668 | 487 | 30673 | Not Used (255) | NO VANES SENSOR
30668 | 488 | 30673 | Not Used (255) | VANE CAL CANCEL
30668 | 489 | 30673 | Not Used (255) | CMPs OFF-FLOW A
30668 | 490 | 30673 | Not Used (255) | CMPs OFF-FLOW B
30668 | 491 | 30673 | Not Used (255) | LowOilPressDrop
30668 | 492 | 30673 | Not Used (255) | UndulyLowOilPres
30668 | 493 | 30673 | Not Used (255) | UndulyLowOilTemp
30668 | 494 | 30673 | Not Used (255) | Hi Bearing Temp
30668 | 495 | 30673 | Not Used (255) | UndulyHiBearTemp
30668 | 496 | 30673 | Not Used (255) | OilPumpOverload
30668 | 497 | 30673 | Not Used (255) | Chl Water Break
30668 | 498 | 30673 | Not Used (255) | UndulyLoChlWater
30668 | 499 | 30673 | Not Used (255) | Unused 40004.08
30668 | 500 | 30673 | Not Used (255) | Unused 40004.09
30668 | 501 | 30673 | Not Used (255) | UndulyLoMotorAmp
30668 | 502 | 30673 | Not Used (255) | Hi Motr Amps
30668 | 503 | 30673 | Not Used (255) | UndulyHiMtrAmps
30668 | 504 | 30673 | Not Used (255) | Long StartupTime
30668 | 505 | 30673 | Not Used (255) | Coil Overheat
30668 | 506 | 30673 | Not Used (255) | Starter Fault
30668 | 507 | 30673 | Not Used (255) | Low Evap Press
30668 | 508 | 30673 | Not Used (255) | UndulyLoEvapPres
30668 | 509 | 30673 | Not Used (255) | Hi Cond Press
30668 | 510 | 30673 | Not Used (255) | UndulyHiCondPres
30668 | 511 | 30673 | Not Used (255) | IGV Fault
30668 | 512 | 30673 | Not Used (255) | Unused 40005.05
30668 | 513 | 30673 | Not Used (255) | Unused 40005.06
30668 | 514 | 30673 | Not Used (255) | Unused 40005.07
30668 | 515 | 30673 | Not Used (255) | Unused 40005.08
30668 | 516 | 30673 | Not Used (255) | Unused 40005.09
30668 | 517 | 30673 | Not Used (255) | Unused 40005.10
30668 | 518 | 30673 | Not Used (255) | Unused 40005.11
30668 | 519 | 30673 | Not Used (255) | Unused 40005.12
30668 | 520 | 30673 | Not Used (255) | Unused 40005.13
30668 | 521 | 30673 | Not Used (255) | Unused 40005.14
30668 | 522 | 30673 | Not Used (255) | Unused 40005.15
30668 | 523 | 30673 | Not Used (255) | ECDWT Break
30668 | 524 | 30673 | Not Used (255) | LCDWT Break
30668 | 525 | 30673 | Not Used (255) | ECWT Break
30668 | 526 | 30673 | Not Used (255) | LCWT Break
30668 | 527 | 30673 | Not Used (255) | OilSumpTempBreak
30668 | 528 | 30673 | Not Used (255) | Unused 40006.05
30668 | 529 | 30673 | Not Used (255) | Cond Press Break
30668 | 530 | 30673 | Not Used (255) | Evap Press Break
30668 | 531 | 30673 | Not Used (255) | OilSpplyPSIBreak
30668 | 532 | 30673 | Not Used (255) | OilSumpPSIBreak
30668 | 533 | 30673 | Not Used (255) | BearingTempBreak
30668 | 534 | 30673 | Not Used (255) | IGV Break
30668 | 535 | 30673 | Not Used (255) | Unused 40006.12
30668 | 536 | 30673 | Not Used (255) | Motor Amp Break
30668 | 537 | 30673 | Not Used (255) | Unused 40006.14
30668 | 538 | 30673 | Not Used (255) | Unused 40006.15
30668 | 539 | 30673 | Not Used (255) | SERVICE TRIP
30668 | 540 | 30673 | Not Used (255) | SERVICE TRIP
30668 | 541 | 30673 | Not Used (255) | SERVICE TRIP
30668 | 542 | 30673 | Not Used (255) | SERVICE TRIP
30668 | 543 | 30673 | Not Used (255) | SERVICE TRIP
30668 | 544 | 30673 | Not Used (255) | NO FLOW
30668 | 545 | 30673 | Not Used (255) | DRY PUMP
30668 | 546 | 30673 | Not Used (255) | END OF CURVE
30668 | 547 | 30673 | Not Used (255) | BROKEN BELT
30668 | 548 | 30673 | Not Used (255) | DISCHARGE HIGH
30668 | 549 | 30673 | Not Used (255) | START FAILED
30668 | 550 | 30673 | Not Used (255) | SPEED LIMIT
30668 | 551 | 30673 | Not Used (255) | EXT INTERLOCK
30668 | 552 | 30673 | Not Used (255) | ILLEGAL OPTNCOMB
30668 | 553 | 30673 | Not Used (255) | NO SAFETY OPTION
30668 | 554 | 30673 | Not Used (255) | UNUSED
30668 | 555 | 30673 | Not Used (255) | UNUSED
30668 | 556 | 30673 | Not Used (255) | KTY ERROR
30668 | 557 | 30673 | Not Used (255) | FANS ERROR
30668 | 558 | 30673 | Not Used (255) | ECB ERROR
30668 | 559 | 30673 | Not Used (255) | UNUSED
30668 | 560 | 30673 | Not Used (255) | UNUSED
30668 | 561 | 30673 | Not Used (255) | UNUSED
30668 | 562 | 30673 | Not Used (255) | UNUSED
30668 | 563 | 30673 | Not Used (255) | UNUSED
30668 | 564 | 30673 | Not Used (255) | CURRENT LIMIT
30668 | 565 | 30673 | Not Used (255) | UNUSED
30668 | 566 | 30673 | Not Used (255) | UNUSED
30668 | 567 | 30673 | Not Used (255) | UNUSED
30668 | 568 | 30673 | Not Used (255) | ENCODER LOSS
30668 | 569 | 30673 | Not Used (255) | PTC THERMISTOR
30668 | 570 | 30673 | Not Used (255) | DANGER FAILURE
30668 | 571 | 30673 | Not Used (255) | Brake check
30668 | 572 | 30673 | Not Used (255) | Pwr card temp
30668 | 573 | 30673 | Not Used (255) | Earth Fault
30668 | 574 | 30673 | Not Used (255) | Ctrl card temp
30668 | 575 | 30673 | Not Used (255) | Ctrl word TO
30668 | 576 | 30673 | Not Used (255) | Over Current
30668 | 577 | 30673 | Not Used (255) | Torque limit
30668 | 578 | 30673 | Not Used (255) | Motor th over
30668 | 579 | 30673 | Not Used (255) | Motor ETR over
30668 | 580 | 30673 | Not Used (255) | Inverter overld
30668 | 581 | 30673 | Not Used (255) | DC under volt
30668 | 582 | 30673 | Not Used (255) | DC over volt
30668 | 583 | 30673 | Not Used (255) | DC voltage low
30668 | 584 | 30673 | Not Used (255) | DC voltage high
30668 | 585 | 30673 | Not Used (255) | Mains ph loss
30668 | 586 | 30673 | Not Used (255) | No motor
30668 | 587 | 30673 | Not Used (255) | Live zero error
30668 | 588 | 30673 | Not Used (255) | 10V low
30668 | 589 | 30673 | Not Used (255) | Brake overload
30668 | 590 | 30673 | Not Used (255) | Brake resistor
30668 | 591 | 30673 | Not Used (255) | Brake IGBT
30668 | 592 | 30673 | Not Used (255) | Speed limit
30668 | 593 | 30673 | Not Used (255) | Fieldbus fault
30668 | 594 | 30673 | Not Used (255) | 24V supply low
30668 | 595 | 30673 | Not Used (255) | Mains failure
30668 | 596 | 30673 | Not Used (255) | Current limit
30668 | 597 | 30673 | Not Used (255) | Low temp
30668 | 598 | 30673 | Not Used (255) | Voltage limit
30668 | 599 | 30673 | Not Used (255) | Encoder loss
30668 | 600 | 30673 | Not Used (255) | Output freq lim
30668 | 601 | 30673 | Not Used (255) | SafeStop
30668 | 602 | 30673 | Not Used (255) | Extnd stat word
30668 | 603 | 30673 | Not Used (255) | Start Delayed
30668 | 604 | 30673 | Not Used (255) | Stop Delayed
30668 | 605 | 30673 | Not Used (255) | Clock Failure
30668 | 606 | 30673 | Not Used (255) | Fire Md was Actv
30668 | 607 | 30673 | Not Used (255) | UNUSED
30668 | 608 | 30673 | Not Used (255) | No Flow
30668 | 609 | 30673 | Not Used (255) | Dry Pump
30668 | 610 | 30673 | Not Used (255) | End of Curve
30668 | 611 | 30673 | Not Used (255) | Broken Belt
30668 | 612 | 30673 | Not Used (255) | Discharge High
30668 | 613 | 30673 | Not Used (255) | Multimotor undld
30668 | 614 | 30673 | Not Used (255) | Multimotor Ovrld
30668 | 615 | 30673 | Not Used (255) | Cmp Interlock
30668 | 616 | 30673 | Not Used (255) | Mech Brk Sliding
30668 | 617 | 30673 | Not Used (255) | Safe Opt Warning
30668 | 618 | 30673 | Not Used (255) | Auto DC Braking
30668 | 619 | 30673 | Not Used (255) | UNUSED
30668 | 620 | 30673 | Not Used (255) | KTY warn
30668 | 621 | 30673 | Not Used (255) | Fans warn
30668 | 622 | 30673 | Not Used (255) | ECB warn
30668 | 623 | 30673 | Not Used (255) | UNUSED
30668 | 624 | 30673 | Not Used (255) | UNUSED
30668 | 625 | 30673 | Not Used (255) | UNUSED
30668 | 626 | 30673 | Not Used (255) | UNUSED
30668 | 627 | 30673 | Not Used (255) | UNUSED
30668 | 628 | 30673 | Not Used (255) | UNUSED
30668 | 629 | 30673 | Not Used (255) | UNUSED
30668 | 630 | 30673 | Not Used (255) | UNUSED
30668 | 631 | 30673 | Not Used (255) | UNUSED
30668 | 632 | 30673 | Not Used (255) | UNUSED
30668 | 633 | 30673 | Not Used (255) | PTC Thermistor
30668 | 634 | 30673 | Not Used (255) | UNUSED
30668 | 635 | 30673 | Not Used (255) | ABB-ShortCircuit
30668 | 636 | 30673 | Not Used (255) | ABB-OVER CURRENT
30668 | 637 | 30673 | Not Used (255) | ABB-DC OVERVOLT
30668 | 638 | 30673 | Not Used (255) | ABB-ACS800 TEMP
30668 | 639 | 30673 | Not Used (255) | ABB-EARTH FAULT
30668 | 640 | 30673 | Not Used (255) | ABB-THERMISTOR
30668 | 641 | 30673 | Not Used (255) | ABB-MOTOR TEMP
30668 | 642 | 30673 | Not Used (255) | ABB-SYSTEM FAULT
30668 | 643 | 30673 | Not Used (255) | ABB-UNDER LOAD
30668 | 644 | 30673 | Not Used (255) | ABB-OVER FREQ
30668 | 645 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 646 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 647 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 648 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 649 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 650 | 30673 | Not Used (255) | ABB-UNUSED
30668 | 651 | 30673 | Not Used (255) | ABB-SUPPLY PHASE
30668 | 652 | 30673 | Not Used (255) | ABB-NO MotorData
30668 | 653 | 30673 | Not Used (255) | ABB-DC UNDERVOLT
30668 | 654 | 30673 | Not Used (255) | ABB-RESERVED
30668 | 655 | 30673 | Not Used (255) | ABB-RUN ENABLE
30668 | 656 | 30673 | Not Used (255) | ABB-ENCODER ERR
30668 | 657 | 30673 | Not Used (255) | ABB-I/O COMM ERR
30668 | 658 | 30673 | Not Used (255) | ABB-CTRL B TEMP
30668 | 659 | 30673 | Not Used (255) | ABB-EXTERNAL FLT
30668 | 660 | 30673 | Not Used (255) | ABB-OVER SWFREQ
30668 | 661 | 30673 | Not Used (255) | ABB-AI<MIN FUNC
30668 | 662 | 30673 | Not Used (255) | ABB-PPCC LINK
30668 | 663 | 30673 | Not Used (255) | ABB-COMM. MODULE
30668 | 664 | 30673 | Not Used (255) | ABB-PANEL LOSS
30668 | 665 | 30673 | Not Used (255) | ABB-MOTOR STALL
30668 | 666 | 30673 | Not Used (255) | ABB-MOTOR PHASE
30668 | 667 | 30673 | Not Used (255) | MOTOR PH OVR AMP
30668 | 668 | 30673 | Not Used (255) | DC BUS OVR VOLTS
30668 | 669 | 30673 | Not Used (255) | TURB MTR RSV
30668 | 670 | 30673 | Not Used (255) | MTR HIGH AMP FLT
30668 | 671 | 30673 | Not Used (255) | INV ERR SIG ACT
30668 | 672 | 30673 | Not Used (255) | ROTOR MAY BE LCK
30668 | 673 | 30673 | Not Used (255) | BEARING FLT ACT
30668 | 674 | 30673 | Not Used (255) | TURB MTR RSV
30668 | 675 | 30673 | Not Used (255) | OUT VLTS NO AMPS
30668 | 676 | 30673 | Not Used (255) | DC VLTS LOW LMT
30668 | 677 | 30673 | Not Used (255) | 24VDC OUT OF RNG
30668 | 678 | 30673 | Not Used (255) | LOW MTR BACK EMF
30668 | 679 | 30673 | Not Used (255) | EEPROM CSUM ERR
30668 | 680 | 30673 | Not Used (255) | GEN MODE ACTIVE
30668 | 681 | 30673 | Not Used (255) | SCR PHASE LOSS
30668 | 682 | 30673 | Not Used (255) | CMP IN STARTUP
30668 | 683 | 30673 | Not Used (255) | CALIBRATION FAIL
30668 | 684 | 30673 | Not Used (255) | STARTUP CK FAIL
30668 | 685 | 30673 | Not Used (255) | AX DISPLACEMENT
30668 | 686 | 30673 | Not Used (255) | AX STATIC LOAD
30668 | 687 | 30673 | Not Used (255) | FRONT RAD DISP X
30668 | 688 | 30673 | Not Used (255) | FRONT RAD DISP Y
30668 | 689 | 30673 | Not Used (255) | FRNT RD ST LD X
30668 | 690 | 30673 | Not Used (255) | FRNT RD ST LD Y
30668 | 691 | 30673 | Not Used (255) | REAR RAD DISP X
30668 | 692 | 30673 | Not Used (255) | REAR RAD DISP Y
30668 | 693 | 30673 | Not Used (255) | REAR RD ST LD X
30668 | 694 | 30673 | Not Used (255) | REAR RD ST LD Y
30668 | 695 | 30673 | Not Used (255) | TURB BEARING RSV
30668 | 696 | 30673 | Not Used (255) | TURB BEARING RSV
30668 | 697 | 30673 | Not Used (255) | TURB BEARING RSV
30668 | 698 | 30673 | Not Used (255) | TURB BEARING RSV
30668 | 699 | 30673 | Not Used (255) | MBC NOT ALIVE
30668 | 700 | 30673 | Not Used (255) | MBC NOT READY
30668 | 701 | 30673 | Not Used (255) | MBC THD Alarm
30668 | 702 | 30673 | Not Used (255) | MBC BEARING1
30668 | 703 | 30673 | Not Used (255) | MBC BEARING2
30668 | 704 | 30673 | Not Used (255) | MBC NoOkRotate
Comp Number | Comp ID
1 | 1