## LCWX1- 0385F
Controller Type | Device Type
LCWX1-0385F | CHILLER
Parameter Display Name | Function Code | Register Address | Slave ID | Baud Rate Code | Display Group | Display Order | Starting Bit | Data Length | Multiplier | Format | Category | Trend Required | Control Category | Minimum Threshold | Maximum Threshold | Unit | Access Control | Status
Compressor 1 On/Off Relay | 01 | 00001 | 01 | 9600 | Relay-Outputs | 1 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Load Solenoid Valve 1 Relay | 01 | 00002 | 01 | 9600 | Relay-Outputs | 2 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Unload Solenoid Valve 1 Relay | 01 | 00003 | 01 | 9600 | Relay-Outputs | 3 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Orifice Solenoid Valve 1 Relay | 01 | 00004 | 01 | 9600 | Relay-Outputs | 4 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Economizer Solenoid Valve 1 Relay | 01 | 00005 | 01 | 9600 | Relay-Outputs | 5 |  | 2 | 1 | BINARY | BINARY | Yes | [5 empty] | 0=Off¦1=On
Alarm Relay | 01 | 00010 | 01 | 9600 | Relay-Outputs | 6 |  | 2 | 1 | BINARY | BINARY | Yes
Suction Pressure | 04 | 30001 | 01 | 9600 | Analog-Inputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 25 | 70 | PSIG
Discharge Pressure | 04 | 30002 | 01 | 9600 | Analog-Inputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 149 | PSIG
Oil Pressure | 04 | 30003 | 01 | 9600 | Analog-Inputs | 3 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 95 | 145 | PSIG
Cooler Water Out Temp | 04 | 30004 | 01 | 9600 | Analog-Inputs | 4 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 39 | 75 | F
Cooler Water In Temp | 04 | 30005 | 01 | 9600 | Analog-Inputs | 5 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 44 | 85 | F
Compressor Current | 04 | 30006 | 01 | 9600 | Analog-Inputs | 6 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | A
Suction Temperature | 04 | 30007 | 01 | 9600 | Analog-Inputs | 7 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 34 | 75 | F
Discharge Temperature | 04 | 30008 | 01 | 9600 | Analog-Inputs | 8 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 100 | 149 | F
Level Transducer | 04 | 30009 | 01 | 9600 | Analog-Inputs | 9 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 11 | 60 | %
PT 1000 | 04 | 30010 | 01 | 9600 | Analog-Inputs | 10 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 65 | 130 | F
Condenser Water In Temp | 04 | 30011 | 01 | 9600 | Analog-Inputs | 11 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  | 50 | 100 | F
Flow Switch | 04 | 30013 | 01 | 9600 | Digital-Inputs | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Oil level switch | 04 | 30014 | 01 | 9600 | Digital-Inputs | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Unit Switch | 04 | 30015 | 01 | 9600 | Digital-Inputs | 3 |  | 4 | 1 | DECIMAL | Status | Yes
SPPR | 04 | 30016 | 01 | 9600 | Digital-Inputs | 4 |  | 4 | 1 | DECIMAL | Status | Yes
Electronic Expansion Valve | 04 | 30201 | 01 | 9600 | Analog-Outputs | 1 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
CND valve % | 04 | 30203 | 01 | 9600 | Analog-Outputs | 2 |  | 4 | 0.1 | DECIMAL | Periodic | Yes |  |  |  | %
Chiller State | 04 | 30306 | 01 | 9600 | Control-Information | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Comp 1 State | 04 | 30307 | 01 | 9600 | Control-Information | 2 |  | 4 | 1 | DECIMAL | Status | Yes
Steps Wanted | 04 | 30315 | 01 | 9600 | Control-Information | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes
Steps On | 04 | 30316 | 01 | 9600 | Control-Information | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes
Step Delay | 04 | 30317 | 01 | 9600 | Control-Information | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Sec
Wanted FLA | 04 | 30318 | 01 | 9600 | Control-Information | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Comp FLA | 04 | 30319 | 01 | 9600 | Control-Information | 7 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | %
Saturated Suction Temp | 04 | 30327 | 01 | 9600 | Analog-Inputs | 15 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Suction Superheat | 04 | 30328 | 01 | 9600 | Analog-Inputs | 16 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 0 | 12 | F
Saturated Discharge Temp | 04 | 30329 | 01 | 9600 | Analog-Inputs | 17 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | F
Discharge Superheat | 04 | 30330 | 01 | 9600 | Analog-Inputs | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  | 14 | 26 | F
Oil Pressure Diff | 04 | 30375 | 01 | 9600 | Analog-Inputs | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | Yes |  |  |  | PSIG
Unit Mode | 04 | 30758 | 01 | 9600 | Control-Information | 8 |  | 4 | 1 | DECIMAL | Status | Yes
Alarm Type | 04 | 30668 | 01 | 9600 | Alarm | 1 |  | 4 | 1 | DECIMAL | Status | Yes
Alarm Point | 04 | 30673 | 01 | 9600 | Alarm | 2 |  | 4 | 1 | DECIMAL | Status | Yes
RH Compressor 1 On/Off | 04 | 30678 | 01 | 9600 | Runhours | 1 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Load Solenoid Valve 1 | 04 | 30679 | 01 | 9600 | Runhours | 2 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Unload Solenoid Valve 1 | 04 | 30680 | 01 | 9600 | Runhours | 3 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Orifice Solenoid Valve 1 | 04 | 30681 | 01 | 9600 | Runhours | 4 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Economizer Solenoid Valve 1 | 04 | 30682 | 01 | 9600 | Runhours | 5 |  | 4 | 1 | DECIMAL | Periodic | Yes |  |  |  | Hrs.
RH Alarm | 04 | 30687 | 01 | 9600 | Runhours | 6 |  | 4 | 1 | DECIMAL | Periodic | Yes
CW OUT TRGT | 03 | 40301 | 01 | 9600 | Setpoints | 1 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
CTRL ZONE+ | 03 | 40302 | 01 | 9600 | Setpoints | 2 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
CTRL ZONE- | 03 | 40303 | 01 | 9600 | Setpoints | 3 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
REF LVL TARG | 03 | 40309 | 01 | 9600 | Setpoints | 4 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
REF LVL ZONE | 03 | 40310 | 01 | 9600 | Setpoints | 5 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV LOAD ADJ | 03 | 40311 | 01 | 9600 | Setpoints | 6 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV FINE ADJ | 03 | 40312 | 01 | 9600 | Setpoints | 7 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV COURSE | 03 | 40313 | 01 | 9600 | Setpoints | 8 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
EXV Load DIV | 03 | 40314 | 01 | 9600 | Setpoints | 9 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint
EXV MIN% | 03 | 40315 | 01 | 9600 | Setpoints | 10 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
EXV MAX% | 03 | 40316 | 01 | 9600 | Setpoints | 11 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOSUCTPSIDLY | 03 | 40318 | 01 | 9600 | Setpoints | 12 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV DELAY | 03 | 40319 | 01 | 9600 | Setpoints | 13 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
EXV STRT TME | 03 | 40320 | 01 | 9600 | Setpoints | 14 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
POWERUP DLAY | 03 | 40323 | 01 | 9600 | Setpoints | 15 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
STEP SENSIT | 03 | 40325 | 01 | 9600 | Setpoints | 16 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
STEP DELAY | 03 | 40326 | 01 | 9600 | Setpoints | 17 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX ROC- | 03 | 40327 | 01 | 9600 | Setpoints | 18 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
MAX ROC+ | 03 | 40328 | 01 | 9600 | Setpoints | 19 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | F
ROC INTERVAL | 03 | 40329 | 01 | 9600 | Setpoints | 20 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
MAX FLA % | 03 | 40330 | 01 | 9600 | Setpoints | 21 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN FLA % | 03 | 40331 | 01 | 9600 | Setpoints | 22 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MAX ADJUST % | 03 | 40332 | 01 | 9600 | Setpoints | 23 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
MIN ADJUST % | 03 | 40333 | 01 | 9600 | Setpoints | 24 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
SLIDE SENSIT | 03 | 40334 | 01 | 9600 | Setpoints | 25 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
AMP DB HI | 03 | 40335 | 01 | 9600 | Setpoints | 26 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
AMP DB LO | 03 | 40336 | 01 | 9600 | Setpoints | 27 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
LOAD PULSE | 03 | 40337 | 01 | 9600 | Setpoints | 28 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint
UNLOAD PULSE | 03 | 40338 | 01 | 9600 | Setpoints | 29 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint
CND DELAY | 03 | 40348 | 01 | 9600 | Setpoints | 30 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
CNDVLVstart% | 03 | 40349 | 01 | 9600 | Setpoints | 31 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CND VLV TARG | 03 | 40350 | 01 | 9600 | Setpoints | 32 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | PSIG
CND VLV DIV | 03 | 40351 | 01 | 9600 | Setpoints | 33 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint
CND VLV MIN | 03 | 40352 | 01 | 9600 | Setpoints | 34 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | %
CND VLV ROC- | 03 | 40353 | 01 | 9600 | Setpoints | 35 |  | 4 | 0.1 | DECIMALSIGNED | Periodic | No | Setpoint |  |  | PSIG
CND VLV MULT | 03 | 40354 | 01 | 9600 | Setpoints | 36 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
CND VLV ADJ | 03 | 40355 | 01 | 9600 | Setpoints | 37 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
PULSE DELAY | 03 | 40356 | 01 | 9600 | Setpoints | 38 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
A-CYC OFF-ON | 03 | 40359 | 01 | 9600 | Setpoints | 39 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
PMP DWN OFF | 03 | 40361 | 01 | 9600 | Setpoints | 40 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
PMP DWN DLAY | 03 | 40362 | 01 | 9600 | Setpoints | 41 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
A-CYC ON-ON | 03 | 40363 | 01 | 9600 | Setpoints | 42 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
COMP MIN RUN | 03 | 40364 | 01 | 9600 | Setpoints | 43 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Min
HI AMPS % | 03 | 40375 | 01 | 9600 | Setpoints | 44 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOampNoSTART | 03 | 40376 | 01 | 9600 | Setpoints | 45 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
LOW SUCTION | 03 | 40377 | 01 | 9600 | Setpoints | 46 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT UNLD | 03 | 40378 | 01 | 9600 | Setpoints | 47 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO SUCT RELD | 03 | 40379 | 01 | 9600 | Setpoints | 48 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LOgas/LLsFLT | 03 | 40380 | 01 | 9600 | Setpoints | 49 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC PSI | 03 | 40381 | 01 | 9600 | Setpoints | 50 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC UNLD | 03 | 40382 | 01 | 9600 | Setpoints | 51 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI DISC RELD | 03 | 40383 | 01 | 9600 | Setpoints | 52 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LO DiscSPRHT | 03 | 40384 | 01 | 9600 | Setpoints | 53 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
HI DISCH TMP | 03 | 40387 | 01 | 9600 | Setpoints | 54 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP UNLD | 03 | 40388 | 01 | 9600 | Setpoints | 55 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
DIS TMP RELD | 03 | 40389 | 01 | 9600 | Setpoints | 56 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LOW OIL DIF | 03 | 40391 | 01 | 9600 | Setpoints | 57 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
UNSAFE OIL | 03 | 40392 | 01 | 9600 | Setpoints | 58 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
HI Motor TMP | 03 | 40394 | 01 | 9600 | Setpoints | 59 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
SPPR Fault | 03 | 40395 | 01 | 9600 | Setpoints | 60 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
DIRTY FILTER | 03 | 40397 | 01 | 9600 | Setpoints | 61 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
LLS-ORIF-ON% | 03 | 40398 | 01 | 9600 | Setpoints | 62 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
ERCON ON% | 03 | 40399 | 01 | 9600 | Setpoints | 63 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
SafetyHold | 03 | 40401 | 01 | 9600 | Setpoints | 64 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | Sec
HI REF LVL | 03 | 40409 | 01 | 9600 | Setpoints | 65 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | %
FREEZE | 03 | 40411 | 01 | 9600 | Setpoints | 66 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
LowOil Level | 03 | 40439 | 01 | 9600 | Setpoints | 67 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
FLA COMP#1 | 03 | 40471 | 01 | 9600 | Setpoints | 70 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | A
HI EVP DEL T | 03 | 40502 | 01 | 9600 | Setpoints | 71 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | F
MDP OIL DIFF | 03 | 40505 | 01 | 9600 | Setpoints | 72 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG
No OIL Flow | 03 | 40511 | 01 | 9600 | Setpoints | 73 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint
OIL FlowDiff | 03 | 40521 | 01 | 9600 | Setpoints | 74 |  | 4 | 0.1 | DECIMAL | Periodic | No | Setpoint |  |  | PSIG

## Status
Register Address | State |  |  | Description
30013 | 0 |  |  | NO FLOW
30013 | 1 |  |  | FLOW
30014 | 0 |  |  | OK
30014 | 1 |  |  | TRIP
30015 | 0 |  |  | ON
30015 | 1 |  |  | OFF
30016 | 0 |  |  | NORMAL
30016 | 1 |  |  | ALARM
30306 | 0 |  |  | UNIT IN POWER UP
30306 | 1 |  |  | POWER LOSS DELAY
30306 | 2 |  |  | NO RUN- I/O LOST
30306 | 3 |  |  | UNIT IN LOCKOUT
30306 | 4 |  |  | UNIT IS OFF
30306 | 5 |  |  | UNIT IS HOLDING
30306 | 6 |  |  | UNIT UNLOADING
30306 | 7 |  |  | UNIT IS LOADING
30306 | 8 |  |  | OFF-SMOKE ALARM
30306 | 9 |  |  | RUN/STOP SW OFF
30306 | 10 |  |  | SCHEDULED OFF
30306 | 11 |  |  | OFF-NO FLOW(s)
30306 | 12 |  |  | NOT USED
30306 | 13 |  |  | AMBIENT OFF
30306 | 14 |  |  | PROCESS HEAT OFF
30306 | 15 |  |  | UNIT IS UNLOADED
30306 | 16 |  |  | UNIT IS LOADED
30306 | 17 |  |  | OFF TMP-ICE MADE
30306 | 18 |  |  | ECONOMIZER ONLY
30306 | 19 |  |  | SWITCHING MODES
30306 | 20 |  |  | UNIT SMOKE UNLDG
30306 | 21 |  |  | UNIT OFF UNLDING
30306 | 22 |  |  | UNIT DMD UNLDING
30306 | 23 |  |  | UNIT HEAT UNLDNG
30306 | 24 |  |  | UNLDING RUN CMPS
30306 | 25 |  |  | OPENING BYP VLV
30306 | 26 |  |  | CMP RAMPING UP
30306 | 27 |  |  | CLOSING BYP VLV
30306 | 28 |  |  | FACTORY STARTUP
30306 | 29 |  |  | MAXIMUM RUN TIME
30306 | 30 |  |  | NOT USED
30306 | 31 |  |  | OFF-FIRE ALARM
30306 | 32 |  |  | UNIT HEAT HOLDG
30306 | 33 |  |  | CMP SPD OPTIMIZE
30307 | 0 |  |  | LOST IO LOCKED
30307 | 1 |  |  | CMP LOCKED OUT
30307 | 2 |  |  | SWITCHED OFF
30307 | 3 |  |  | UNLD & PMPDWN
30307 | 4 |  |  | CMP ANTICYCLE
30307 | 5 |  |  | CMP OFF/READY
30307 | 6 |  |  | OIL PMP LUBING
30307 | 7 |  |  | CMP IN STARTUP
30307 | 8 |  |  | CMP UNLOADED
30307 | 9 |  |  | CMP UNLD STEP1
30307 | 10 |  |  | CMP UNLD STEP2
30307 | 11 |  |  | CMP IS HOLDING
30307 | 12 |  |  | CMP IS LOADING
30307 | 13 |  |  | CMP IS UNLDING
30307 | 14 |  |  | CMP IS RUNNING
30307 | 15 |  |  | FAST UNLOADING
30307 | 16 |  |  | LO SUCT UNLOAD
30307 | 17 |  |  | LO SUCT HOLD
30307 | 18 |  |  | HI DISC UNLOAD
30307 | 19 |  |  | HI DISC HOLD
30307 | 20 |  |  | SAFETY TRIPPED
30307 | 21 |  |  | LO TEMP UNLOAD
30307 | 22 |  |  | LO TEMP HOLD
30307 | 23 |  |  | HI AMP HOLD
30307 | 24 |  |  | HI DIS TMP HLD
30307 | 25 |  |  | CMP IS AT 40%
30307 | 26 |  |  | CMP IS AT 70%
30307 | 27 |  |  | HI WATER HOLD
30307 | 28 |  |  | EXTRA 70% STEP
30307 | 29 |  |  | OFF-LO OIL TMP
30307 | 30 |  |  | HI AMP UNLDING
30307 | 31 |  |  | DEF PREPMP OUT
30307 | 32 |  |  | DEFROSTING
30307 | 33 |  |  | DEF PUMP DOWN
30307 | 34 |  |  | HI TEMP UNLOAD
30307 | 35 |  |  | HI TEMP HOLD
30307 | 36 |  |  | SCROLL STEP 1
30307 | 37 |  |  | SCROLL STEP 2
30307 | 38 |  |  | SCROLL STEP 3
30307 | 39 |  |  | SCROLL STEP 4
30307 | 40 |  |  | ON OIL RECOVRY
30307 | 41 |  |  | WAIT P-RATIO
Register Address Type | Status/ Alarm Type | Register Address Point | Alarm Point | Description
30668 | 0 | 30673 | Not Used (255) | POWER FAILED
30668 | 1 | 30673 | Not Used (255) | COMPUTER RESET
30668 | 2 | 30673 | Not Used (255) | BATTERY FAILED
30668 | 3 | 30673 | Not Used (255) | INVERTER TEMP
30668 | 4 | 30673 | Not Used (255) | DISCHARGE TEMP
30668 | 5 | 30673 | Not Used (255) | SUCTION PSI
30668 | 6 | 30673 | Not Used (255) | DISCHARGE PSI
30668 | 7 | 30673 | Not Used (255) | 3PHASE OVER AMPS
30668 | 8 | 30673 | Not Used (255) | ALARMS CLEARED
30668 | 9 | 30673 | Not Used (255) | POWER RETURNED
30668 | 10 | 30673 | Not Used (255) | CAVITY TEMP
30668 | 11 | 30673 | Not Used (255) | STPT CHANGED
30668 | 12 | 30673 | Not Used (255) | RO TO MANON
30668 | 13 | 30673 | Not Used (255) | AO TO MANUAL
30668 | 14 | 30673 | Not Used (255) | SI TO MANUAL
30668 | 15 | 30673 | Not Used (255) | POINT INFO CLEAR
30668 | 16 | 30673 | Not Used (255) | CLOCK SET
30668 | 17 | 30673 | Not Used (255) | CFG DOWNLOADED
30668 | 18 | 30673 | Not Used (255) | ROTATED LEAD\0
30668 | 19 | 30673 | Not Used (255) | SI OFFSET
30668 | 20 | 30673 | Not Used (255) | SI TYPE
30668 | 21 | 30673 | Not Used (255) | LEAV FLUID TEMP
30668 | 22 | 30673 | Not Used (255) | PRESSURE RATIO
30668 | 23 | 30673 | Not Used (255) | BEAR MOTOR CMP
30668 | 24 | 30673 | Not Used (255) | CMP SENSOR FLT
30668 | 25 | 30673 | Not Used (255) | DAYLIGHT SAVINGS
30668 | 26 | 30673 | Not Used (255) | LOCKOUT RESET
30668 | 27 | 30673 | Not Used (255) | FIRMWARE LOADED
30668 | 28 | 30673 | Not Used (255) | BOOTLOADER ERROR
30668 | 29 | 30673 | Not Used (255) | RS486 CHANGED
30668 | 30 | 30673 | Not Used (255) | ETHERNET CHANGED
30668 | 31 | 30673 | Not Used (255) | INVALID CFG CSUM
30668 | 32 | 30673 | Not Used (255) | INVALID CFG VER
30668 | 33 | 30673 | Not Used (255) | LOST RO COMM
30668 | 34 | 30673 | Not Used (255) | LOST SI COMM
30668 | 35 | 30673 | Not Used (255) | BACnet Port Chg
30668 | 36 | 30673 | Not Used (255) | WATCHDOG RESET
30668 | 37 | 30673 | Not Used (255) | SRC TEMP FAULT
30668 | 38 | 30673 | Not Used (255) | EMERGENCY STOP
30668 | 39 | 30673 | Not Used (255) | OFF-SMOKE ALARM
30668 | 40 | 30673 | Not Used (255) | RO TO AUTO
30668 | 41 | 30673 | Not Used (255) | AO TO AUTO
30668 | 42 | 30673 | Not Used (255) | SI TO AUTO
30668 | 43 | 30673 | Not Used (255) | PHASE LOSS
30668 | 44 | 30673 | Not Used (255) | RO TO MANOFF
30668 | 45 | 30673 | Not Used (255) | TURBO LOCK OUT
30668 | 46 | 30673 | Not Used (255) | TURBO WIND TMP
30668 | 47 | 30673 | Not Used (255) | TURBOCOR SSH FLT
30668 | 48 | 30673 | Not Used (255) | TURB RESERVED
30668 | 49 | 30673 | Not Used (255) | CND/CTG FAULT
30668 | 50 | 30673 | Not Used (255) | LOST IO SHUTDOWN
30668 | 51 | 30673 | Not Used (255) | SMOKE PURGE
30668 | 52 | 30673 | Not Used (255) | INVALID CFG TYPE
30668 | 53 | 30673 | Not Used (255) | ENGY WHEEL ALARM
30668 | 54 | 30673 | Not Used (255) | LOST I/O RESTART
30668 | 55 | 30673 | Not Used (255) | OFF-FIRE ALARM
30668 | 56 | 30673 | Not Used (255) | NO IGNITION
30668 | 57 | 30673 | Not Used (255) | PURGE RESTART
30668 | 58 | 30673 | Not Used (255) | TMP OFF-ICE MADE
30668 | 59 | 30673 | Not Used (255) | LVL OFF-ICE MADE
30668 | 60 | 30673 | Not Used (255) | START MAKING ICE
30668 | 61 | 30673 | Not Used (255) | INTERNAL RAM
30668 | 62 | 30673 | Not Used (255) | EXTERNAL RAM 1
30668 | 63 | 30673 | Not Used (255) | EXTERNAL RAM 2
30668 | 64 | 30673 | Not Used (255) | LOST A/D CONVTR
30668 | 65 | 30673 | Not Used (255) | LOST DISPLAY
30668 | 66 | 30673 | Not Used (255) | LOST IO COMP
30668 | 67 | 30673 | Not Used (255) | LOST KEYPAD
30668 | 68 | 30673 | Not Used (255) | CFG FLASH PTR
30668 | 69 | 30673 | Not Used (255) | NETWORK ADDR CHG
30668 | 70 | 30673 | Not Used (255) | UPDATED FLASHCFG
30668 | 71 | 30673 | Not Used (255) | LOST A/D SHUTDWN
30668 | 72 | 30673 | Not Used (255) | CF CARD REMOVED
30668 | 73 | 30673 | Not Used (255) | CF CARD INSERTED
30668 | 74 | 30673 | Not Used (255) | CF INIT ERROR
30668 | 75 | 30673 | Not Used (255) | MCS-STAT OFFLINE
30668 | 76 | 30673 | Not Used (255) | BACnet Addr Chg
30668 | 77 | 30673 | Not Used (255) | FORCE MCS PROCOL
30668 | 78 | 30673 | Not Used (255) | UNUSED ALARM #78
30668 | 79 | 30673 | Not Used (255) | UNUSED ALARM #79
30668 | 80 | 30673 | 1 | CW OUT TRGT
30668 | 81 | 30673 | 1 | CTRL ZONE+
30668 | 82 | 30673 | 1 | CTRL ZONE-
30668 | 83 | 30673 | 1 | Spare
30668 | 84 | 30673 | 1 | Spare
30668 | 85 | 30673 | 1 | Spare
30668 | 86 | 30673 | 1 | Spare
30668 | 87 | 30673 | 1 | Spare
30668 | 88 | 30673 | 1 | REF LVL TARG
30668 | 89 | 30673 | 1 | REF LVL ZONE
30668 | 90 | 30673 | 1 | EXV LOAD ADJ
30668 | 91 | 30673 | 1 | EXV FINE ADJ
30668 | 92 | 30673 | 1 | EXV COURSE
30668 | 93 | 30673 | 1 | EXV Load DIV
30668 | 94 | 30673 | 1 | EXV MIN%
30668 | 95 | 30673 | 1 | EXV MAX%
30668 | 96 | 30673 | 1 | Spare
30668 | 97 | 30673 | 1 | LOSUCTPSIDLY
30668 | 98 | 30673 | 1 | EXV DELAY
30668 | 99 | 30673 | 1 | EXV STRT TME
30668 | 100 | 30673 | 1 | Spare
30668 | 101 | 30673 | 1 | Spare
30668 | 102 | 30673 | 1 | POWERUP DLAY
30668 | 103 | 30673 | 1 | Spare
30668 | 104 | 30673 | 1 | STEP SENSIT
30668 | 105 | 30673 | 1 | STEP DELAY
30668 | 106 | 30673 | 1 | MAX ROC-
30668 | 107 | 30673 | 1 | MAX ROC+
30668 | 108 | 30673 | 1 | ROC INTERVAL
30668 | 109 | 30673 | 1 | MAX FLA %
30668 | 110 | 30673 | 1 | MIN FLA %
30668 | 111 | 30673 | 1 | MAX ADJUST %
30668 | 112 | 30673 | 1 | MIN ADJUST %
30668 | 113 | 30673 | 1 | SLIDE SENSIT
30668 | 114 | 30673 | 1 | AMP DB HI
30668 | 115 | 30673 | 1 | AMP DB LO
30668 | 116 | 30673 | 1 | LOAD PULSE
30668 | 117 | 30673 | 1 | UNLOAD PULSE
30668 | 118 | 30673 | 1 | Spare
30668 | 119 | 30673 | 1 | Spare
30668 | 120 | 30673 | 1 | Spare
30668 | 121 | 30673 | 1 | Spare
30668 | 122 | 30673 | 1 | Spare
30668 | 123 | 30673 | 1 | Spare
30668 | 124 | 30673 | 1 | Spare
30668 | 125 | 30673 | 1 | Spare
30668 | 126 | 30673 | 1 | Spare
30668 | 127 | 30673 | 1 | CND DELAY
30668 | 128 | 30673 | 1 | CNDVLVstart%
30668 | 129 | 30673 | 1 | CND VLV TARG
30668 | 130 | 30673 | 1 | CND VLV DIV
30668 | 131 | 30673 | 1 | CND VLV MIN
30668 | 132 | 30673 | 1 | CND VLV ROC-
30668 | 133 | 30673 | 1 | CND VLV MULT
30668 | 134 | 30673 | 1 | CND VLV ADJ
30668 | 135 | 30673 | 1 | PULSE DELAY
30668 | 136 | 30673 | 1 | Spare
30668 | 137 | 30673 | 1 | Spare
30668 | 138 | 30673 | 1 | A-CYC OFF-ON
30668 | 139 | 30673 | 1 | Spare
30668 | 140 | 30673 | 1 | PMP DWN OFF
30668 | 141 | 30673 | 1 | PMP DWN DLAY
30668 | 142 | 30673 | 1 | A-CYC ON-ON
30668 | 143 | 30673 | 1 | COMP MIN RUN
30668 | 144 | 30673 | 1 | Spare
30668 | 145 | 30673 | 1 | Spare
30668 | 146 | 30673 | 1 | Spare
30668 | 147 | 30673 | 1 | Spare
30668 | 148 | 30673 | 1 | Spare
30668 | 149 | 30673 | 1 | Spare
30668 | 150 | 30673 | 1 | Spare
30668 | 151 | 30673 | 1 | Spare
30668 | 152 | 30673 | 1 | Spare
30668 | 153 | 30673 | 1 | Spare
30668 | 154 | 30673 | 1 | HI AMPS %
30668 | 155 | 30673 | 1 | LOampNoSTART
30668 | 156 | 30673 | 1 | LOW SUCTION
30668 | 157 | 30673 | 1 | LO SUCT UNLD
30668 | 158 | 30673 | 1 | LO SUCT RELD
30668 | 159 | 30673 | 1 | LOgas/LLsFLT
30668 | 160 | 30673 | 1 | HI DISC PSI
30668 | 161 | 30673 | 1 | HI DISC UNLD
30668 | 162 | 30673 | 1 | HI DISC RELD
30668 | 163 | 30673 | 1 | LO DiscSPRHT
30668 | 164 | 30673 | 1 | Spare
30668 | 165 | 30673 | 1 | Spare
30668 | 166 | 30673 | 1 | HI DISCH TMP
30668 | 167 | 30673 | 1 | DIS TMP UNLD
30668 | 168 | 30673 | 1 | DIS TMP RELD
30668 | 169 | 30673 | 1 | Spare
30668 | 170 | 30673 | 1 | LOW OIL DIF
30668 | 171 | 30673 | 1 | UNSAFE OIL
30668 | 172 | 30673 | 1 | Spare
30668 | 173 | 30673 | 1 | HI Motor TMP
30668 | 174 | 30673 | 1 | SPPR Fault
30668 | 175 | 30673 | 1 | Spare
30668 | 176 | 30673 | 1 | DIRTY FILTER
30668 | 177 | 30673 | 1 | Spare
30668 | 178 | 30673 | 1 | ERCON ON%
30668 | 179 | 30673 | 1 | Spare
30668 | 180 | 30673 | 1 | SafetyHold
30668 | 181 | 30673 | 1 | Spare
30668 | 182 | 30673 | 1 | Spare
30668 | 183 | 30673 | 1 | Spare
30668 | 184 | 30673 | 1 | Spare
30668 | 185 | 30673 | 1 | Spare
30668 | 186 | 30673 | 1 | Spare
30668 | 187 | 30673 | 1 | Spare
30668 | 188 | 30673 | 1 | HI REF LVL
30668 | 189 | 30673 | 1 | Spare
30668 | 190 | 30673 | 1 | FREEZE
30668 | 191 | 30673 | 1 | Spare
30668 | 192 | 30673 | 1 | Spare
30668 | 193 | 30673 | 1 | Spare
30668 | 194 | 30673 | 1 | Spare
30668 | 195 | 30673 | 1 | Spare
30668 | 196 | 30673 | 1 | Spare
30668 | 197 | 30673 | 1 | Spare
30668 | 198 | 30673 | 1 | Spare
30668 | 199 | 30673 | 1 | Spare
30668 | 200 | 30673 | 1 | Spare
30668 | 201 | 30673 | 1 | Spare
30668 | 202 | 30673 | 1 | Spare
30668 | 203 | 30673 | 1 | Spare
30668 | 204 | 30673 | 1 | Spare
30668 | 205 | 30673 | 1 | Spare
30668 | 206 | 30673 | 1 | Spare
30668 | 207 | 30673 | 1 | Spare
30668 | 208 | 30673 | 1 | Spare
30668 | 209 | 30673 | 1 | Spare
30668 | 210 | 30673 | 1 | Spare
30668 | 211 | 30673 | 1 | Spare
30668 | 212 | 30673 | 1 | Spare
30668 | 213 | 30673 | 1 | Spare
30668 | 214 | 30673 | 1 | Spare
30668 | 215 | 30673 | 1 | Spare
30668 | 216 | 30673 | 1 | Spare
30668 | 217 | 30673 | 1 | Spare
30668 | 218 | 30673 | 1 | LowOil Level
30668 | 219 | 30673 | 1 | Spare
30668 | 220 | 30673 | 1 | Spare
30668 | 221 | 30673 | 1 | Spare
30668 | 222 | 30673 | 1 | Spare
30668 | 223 | 30673 | 1 | Spare
30668 | 224 | 30673 | 1 | Spare
30668 | 225 | 30673 | 1 | Spare
30668 | 226 | 30673 | 1 | Spare
30668 | 227 | 30673 | 1 | Spare
30668 | 228 | 30673 | 1 | Spare
30668 | 229 | 30673 | 1 | Spare
30668 | 230 | 30673 | 1 | Spare
30668 | 231 | 30673 | 1 | Spare
30668 | 232 | 30673 | 1 | Spare
30668 | 233 | 30673 | 1 | Spare
30668 | 234 | 30673 | 1 | Spare
30668 | 235 | 30673 | 1 | Spare
30668 | 236 | 30673 | 1 | Spare
30668 | 237 | 30673 | 1 | Spare
30668 | 238 | 30673 | 1 | Spare
30668 | 239 | 30673 | 1 | Spare
30668 | 240 | 30673 | 1 | Spare
30668 | 241 | 30673 | 1 | Spare
30668 | 242 | 30673 | 1 | Spare
30668 | 243 | 30673 | 1 | Spare
30668 | 244 | 30673 | 1 | Spare
30668 | 245 | 30673 | 1 | Spare
30668 | 246 | 30673 | 1 | Spare
30668 | 247 | 30673 | 1 | Spare
30668 | 248 | 30673 | 1 | Spare
30668 | 249 | 30673 | 1 | Spare
30668 | 250 | 30673 | 1 | FLA COMP#1
30668 | 251 | 30673 | 1 | Spare
30668 | 252 | 30673 | 1 | Spare
30668 | 253 | 30673 | 1 | Spare
30668 | 254 | 30673 | 1 | Spare
30668 | 255 | 30673 | 1 | Spare
30668 | 256 | 30673 | 1 | Spare
30668 | 257 | 30673 | 1 | Spare
30668 | 258 | 30673 | 1 | Spare
30668 | 259 | 30673 | 1 | Spare
30668 | 260 | 30673 | 1 | Spare
30668 | 261 | 30673 | 1 | Spare
30668 | 262 | 30673 | 1 | Spare
30668 | 263 | 30673 | 1 | Spare
30668 | 264 | 30673 | 1 | Spare
30668 | 265 | 30673 | 1 | Spare
30668 | 266 | 30673 | 1 | Spare
30668 | 267 | 30673 | 1 | Spare
30668 | 268 | 30673 | 1 | Spare
30668 | 269 | 30673 | 1 | Spare
30668 | 270 | 30673 | 1 | Spare
30668 | 271 | 30673 | 1 | Spare
30668 | 272 | 30673 | 1 | Spare
30668 | 273 | 30673 | 1 | Spare
30668 | 274 | 30673 | 1 | Spare
30668 | 275 | 30673 | 1 | Spare
30668 | 276 | 30673 | 1 | Spare
30668 | 277 | 30673 | 1 | Spare
30668 | 278 | 30673 | 1 | Spare
30668 | 279 | 30673 | 1 | Spare
30668 | 280 | 30673 | 1 | Spare
30668 | 281 | 30673 | 1 | HI EVP DEL T
30668 | 282 | 30673 | 1 | Spare
30668 | 283 | 30673 | 1 | Spare
30668 | 284 | 30673 | 1 | MDP OIL DIFF
30668 | 285 | 30673 | 1 | Spare
30668 | 286 | 30673 | 1 | Spare
30668 | 287 | 30673 | 1 | Spare
30668 | 288 | 30673 | 1 | Spare
30668 | 289 | 30673 | 1 | Spare
30668 | 290 | 30673 | 1 | No OIL Flow
30668 | 291 | 30673 | 1 | Spare
30668 | 292 | 30673 | 1 | Spare
30668 | 293 | 30673 | 1 | Spare
30668 | 294 | 30673 | 1 | Spare
30668 | 295 | 30673 | 1 | Spare
30668 | 296 | 30673 | 1 | Spare
30668 | 297 | 30673 | 1 | Spare
30668 | 298 | 30673 | 1 | Spare
30668 | 299 | 30673 | 1 | Spare
30668 | 300 | 30673 | 1 | OIL FlowDiff
30668 | 301 | NA | 1 | Reserved 222
30668 | 302 | NA | 1 | Reserved 223
30668 | 303 | NA | 1 | Reserved 224
30668 | 304 | NA | 1 | Reserved 225
30668 | 305 | NA | 1 | Reserved 226
30668 | 306 | NA | 1 | Reserved 227
30668 | 307 | NA | 1 | Reserved 228
30668 | 308 | NA | 1 | Reserved 229
30668 | 309 | NA | 1 | Reserved 220
30668 | 310 | 30673 | 0 | Alarm SP1
30668 | 310 | 30673 | 1 | Alarm DP1
30668 | 310 | 30673 | 2 | Alarm OP1
30668 | 310 | 30673 | 3 | Alarm WaterOUT
30668 | 310 | 30673 | 4 | Alarm Water IN
30668 | 310 | 30673 | 5 | Alarm AMPS 1
30668 | 310 | 30673 | 6 | Alarm SucTmp1
30668 | 310 | 30673 | 7 | Alarm DiscTmp1
30668 | 310 | 30673 | 8 | Alarm REFLVL1
30668 | 310 | 30673 | 9 | Alarm PT 1000 1
30668 | 310 | 30673 | 10 | Alarm CondW IN
30668 | 310 | 30673 | 11 | Spare
30668 | 310 | 30673 | 12 | Alarm FLOW SW
30668 | 310 | 30673 | 13 | Alarm Oil Lvl 1
30668 | 310 | 30673 | 14 | Alarm SYS1 OFF
30668 | 310 | 30673 | 15 | Spare
30668 | 310 | 30673 | 16 | Spare
30668 | 310 | 30673 | 17 | Spare
30668 | 310 | 30673 | 18 | Spare
30668 | 310 | 30673 | 19 | Spare
30758 | 0 |  | 1 | CHILLER MODE
30758 | 1 |  | 2 | ICE MAKING MODE
30758 | 2 |  | 3 | HEATING MODE
Comp. Number | Comp. ID
1 | 1